## Cover
Cover sheet
Spill frequency enhancement feeder model
Objective
To assess enhancement expenditure related to spill frequency as submitted by companies in their PR19 business plans.
Approach
We assess the investment for this line by using a model which estimates expected capex based on the company requested capex and volume of storage each company is planning to construct. We use the model to estimate our expected costs and apply an efficiency challenge to these estimates. The efficiency challenge is informed by the potential level of efficiency indicated in our model. Where a company’s requested investment level is less than our determination we use the company’s business plan costs.

## Data
Data
Financial data in £m at 2017-18 prices
codecombine | companycode | financialyear | realWWS2004CAS | WWS2004CAS | S3040TCAS | WWS4001 | WWS4003
Code | Company | Year ending 31 March | Storage schemes in the network to reduce spill frequency at CSOs, etc - capex (£m) | Storage schemes in the network to reduce spill frequency at CSOs, etc - capex (£m) | Wholesale wastewater totex (£m) | Volume of storage provided at CSOs, storm tanks, etc to meet spill frequency objectives (m3) | Number of sewage treatment works at which new or additional storage is provided
ANH21 | ANH | 2021 | 1.6011 | 1.6011 | 551.5038 | 1966 | 21
ANH22 | ANH | 2022 | 5.0384 | 5.0384 | 653.128 | 1249 | 15
ANH23 | ANH | 2023 | 1.7269 | 1.7269 | 659.7913 | 2323 | 43
ANH24 | ANH | 2024 | 0 | 0 | 762.5603 | 4971 | 38
ANH25 | ANH | 2025 | 0 | 0 | 701.7612 | 37211 | 34
NES21 | NES | 2021 | 4.341 | 4.341 | 194.719 | 0 | 0
NES22 | NES | 2022 | 4.342 | 4.342 | 225.872 | 0 | 0
NES23 | NES | 2023 | 1.301 | 1.301 | 250.014 | 15 | 1
NES24 | NES | 2024 | 1.301 | 1.301 | 314.523 | 59 | 3
NES25 | NES | 2025 | 1.301 | 1.301 | 258.249 | 192 | 3
NWT21 | NWT | 2021 | 0.36174 | 0.36174 | 557.405 | 0 | 0
NWT22 | NWT | 2022 | 1.8569 | 1.8569 | 584.4168 | 43850 | 2
NWT23 | NWT | 2023 | 3.663 | 3.663 | 527.2379 | 14511 | 7
NWT24 | NWT | 2024 | 21.4211 | 21.4211 | 706.9906 | 345 | 1
NWT25 | NWT | 2025 | 38.631 | 38.631 | 637.0085 | 45508 | 8
SRN21 | SRN | 2021 | 0 | 0 | 462.081 | 10495 | 9
SRN22 | SRN | 2022 | 0.22 | 0.22 | 610.504 | 10495 | 9
SRN23 | SRN | 2023 | 0.22 | 0.22 | 633.113 | 10495 | 9
SRN24 | SRN | 2024 | 0 | 0 | 495.7 | 10495 | 9
SRN25 | SRN | 2025 | 0 | 0 | 408.064 | 10495 | 9
SVT21 | SVT | 2021 | 0 | 0 | 0 | 0 | 0
SVT22 | SVT | 2022 | 0 | 0 | 0 | 0 | 0
SVT23 | SVT | 2023 | 0 | 0 | 0 | 0 | 0
SVT24 | SVT | 2024 | 0 | 0 | 0 | 0 | 0
SVT25 | SVT | 2025 | 0 | 0 | 0 | 0 | 0
SWT21 | SWT | 2021 |  |  |  |  | 0
SWT22 | SWT | 2022 |  |  |  |  | 0
SWT23 | SWT | 2023 |  |  |  |  | 0
SWT24 | SWT | 2024 |  |  |  |  | 0
SWT25 | SWT | 2025 |  |  |  |  | 0
SWB21 | SWB | 2021 | 10.484 | 10.484 | 209.884 | 764 | 16
SWB22 | SWB | 2022 | 10.422 | 10.422 | 205.418 | 584 | 13
SWB23 | SWB | 2023 | 2.148 | 2.148 | 184.163 | 783 | 16
SWB24 | SWB | 2024 | 6.953 | 6.953 | 182.451 | 2249 | 7
SWB25 | SWB | 2025 | 6.602 | 6.602 | 169.172 | 849 | 7
TMS21 | TMS | 2021 | 0 | 0 | 943.2051 | 0 | 0
TMS22 | TMS | 2022 | 0 | 0 | 1059.5586 | 0 | 0
TMS23 | TMS | 2023 | 0 | 0 | 1043.6785 | 6023.6669 | 9
TMS24 | TMS | 2024 | 0 | 0 | 989.8507 | 1581.5422 | 9
TMS25 | TMS | 2025 | 0 | 0 | 960.8748 | 26626.4865 | 16
WSH21 | WSH | 2021 | 9.837 | 9.837 | 358.459 | 0 | 0
WSH22 | WSH | 2022 | 9.721 | 9.721 | 291.941 | 0 | 0
WSH23 | WSH | 2023 | 9.607 | 9.607 | 301.451 | 0 | 0
WSH24 | WSH | 2024 | 9.482 | 9.482 | 290.19 | 0 | 0
WSH25 | WSH | 2025 | 9.373 | 9.373 | 287.054 | 4953 | 13
WSX21 | WSX | 2021 | 6.1084 | 6.1084 | 334.4099 | 0 | 0
WSX22 | WSX | 2022 | 5.2006 | 5.2006 | 310.3582 | 0 | 0
WSX23 | WSX | 2023 | 4.5689 | 4.5689 | 316.2189 | 309 | 5
WSX24 | WSX | 2024 | 5.4805 | 5.4805 | 314.5551 | 1559 | 7
WSX25 | WSX | 2025 | 1.8714 | 1.8714 | 297.6658 | 12127 | 7
YKY21 | YKY | 2021 | 20.564 | 20.564 | 707.065 | 0 | 0
YKY22 | YKY | 2022 | 14.353 | 14.353 | 713.049 | 0 | 0
YKY23 | YKY | 2023 | 10.646 | 10.646 | 603.856 | 8824 | 21
YKY24 | YKY | 2024 | 9.528 | 9.528 | 488.689 | 8824 | 21
YKY25 | YKY | 2025 | 5.744 | 5.744 | 381.367 | 8824 | 21
SVE21 | SVE | 2021 | 3.046 | 3.046 | 560.9359 | 0 | 0
SVE22 | SVE | 2022 | 3.046 | 3.046 | 614.4787 | 0 | 0
SVE23 | SVE | 2023 | 9.139 | 9.139 | 621.223 | 571.184 | 8
SVE24 | SVE | 2024 | 9.139 | 9.139 | 610.5966 | 662.712 | 9
SVE25 | SVE | 2025 | 6.092 | 6.092 | 545.4369 | 1873.668 | 9
HDD21 | HDD | 2021 | 0 | 0 | 4.3491 | 0 | 0
HDD22 | HDD | 2022 | 0 | 0 | 4.8159 | 0 | 0
HDD23 | HDD | 2023 | 0 | 0 | 5.0267 | 0 | 0
HDD24 | HDD | 2024 | 0 | 0 | 6.1395 | 0 | 0
HDD25 | HDD | 2025 | 0 | 0 | 4.5652 | 20 | 1

## Data tables
Data tables
realWWS2004CAS
Storage schemes in the network to reduce spill frequency at CSOs, etc - capex (£m)
| 2021 | 2022 | 2023 | 2024 | 2025 | Total | Wholesale totex | Materiality
ANH | 1.6011 | 5.0384 | 1.7269 | 0 | 0 | 8.3663 | 3328.7444 | 0.2513%
HDD | 0 | 0 | 0 | 0 | 0 | 0 | 24.8964 | 0%
NES | 4.341 | 4.342 | 1.301 | 1.301 | 1.301 | 12.586 | 1243.377 | 1.012%
NWT | 0.36174 | 1.8569 | 3.663 | 21.4211 | 38.631 | 65.9338 | 3013.0589 | 2.188%
SRN | 0 | 0.22 | 0.22 | 0 | 0 | 0.44 | 2609.462 | 0.01686%
SVE | 3.046 | 3.046 | 9.139 | 9.139 | 6.092 | 30.462 | 2952.671 | 1.032%
SWB | 10.484 | 10.422 | 2.148 | 6.953 | 6.602 | 36.609 | 951.088 | 3.849%
TMS | 0 | 0 | 0 | 0 | 0 | 0 | 4997.1677 | 0%
WSH | 9.837 | 9.721 | 9.607 | 9.482 | 9.373 | 48.02 | 1529.095 | 3.14%
WSX | 6.1084 | 5.2006 | 4.5689 | 5.4805 | 1.8714 | 23.2298 | 1573.2079 | 1.477%
YKY | 20.564 | 14.353 | 10.646 | 9.528 | 5.744 | 60.835 | 2894.026 | 2.102%
WWS4001
Volume of storage provided at CSOs, storm tanks, etc to meet spill frequency objectives (m3)
| 2021 | 2022 | 2023 | 2024 | 2025 | Total
ANH | 1966 | 1249 | 2323 | 4971 | 37211 | 47720
HDD | 0 | 0 | 0 | 0 | 20 | 20
NES | 0 | 0 | 15 | 59 | 192 | 266
NWT | 0 | 43850 | 14511 | 345 | 45508 | 104214
SRN | 10495 | 10495 | 10495 | 10495 | 10495 | 52475
SVE | 0 | 0 | 571.184 | 662.712 | 1873.668 | 3107.564
SWB | 764 | 584 | 783 | 2249 | 849 | 5229
TMS | 0 | 0 | 6023.6669 | 1581.5422 | 26626.4865 | 34231.6956
WSH | 0 | 0 | 0 | 0 | 4953 | 4953
WSX | 0 | 0 | 309 | 1559 | 12127 | 13995
YKY | 0 | 0 | 8824 | 8824 | 8824 | 26472

## Analysis
Modelling analysis and determination of cost allowance
Business Plan data
| Company | Storage schemes in the network to reduce spill frequency at CSOs, etc. - capex, 2020/21 to 24/25 | Volume of new or additional storage provided in the sewerage network (WWS4003) | Number of sites in network at which new or additional storage is provided
| ANH | 8.3663 | 2522 | 7
| HDD | 0 | 0 | 0
| NES | 12.586 | 10000 | 1
| NWT | 65.9338 | 43360 | 16
| SRN | 0.44 | 1740 | 4
| SVE | 30.462 | 23234 | 44
| SWB | 36.609 | 30889 | 20
| TMS | 0 | 0 | 0
| WSH | 48.02 | 3089 | 5
| WSX | 23.2298 | 10450 | 13
| YKY | 60.835 | 44000 | 5
Adjusted Business Plan data
| Company | Storage schemes capex plus reallocations | Volume of new or additional storage provided in the sewerage network | Comments
| ANH | 8.3663 | 2522
HDD
| NES | 12.586 | 10000
| NWT | 65.9338 | 43360
| SRN | 0.44 | 94 | Vol adjusted see Deep dive tab
| SVE | 30.462 | 23234
| SWB | 38.622 | 30889 | Investment allocated into line
TMS
| WSH | 13.5 | 3089 | Investment adjusted to correspond to forecast output - see Deep dive tab
| WSX | 23.2298 | 10450
| YKY | 60.835 | 44000
Determination of modelled costs and efficient allowance
| Company | Predicted cost, £m | Efficiency score | Add-back capex | Predicted Efficient Cost, £m
| ANH | 6.7761 | 123.5% |  | 6.0985
| HDD | 0 |  |  | 0
| NES | 19.3441 | 65.06% |  | 17.4097
| NWT | 59.1143 | 111.5% |  | 53.2029
| SRN | 0.55346 | 79.5% |  | 0.49811
| SVE | 36.7581 | 82.87% |  | 33.0823
| SWB | 45.6599 | 84.59% |  | 41.0939
| TMS | 0 |  |  | 0
| WSH | 7.9076 | 170.7% | 20.2201 | 25.3149
| WSX | 20.0035 | 116.1% |  | 18.0032
| YKY | 59.7776 | 101.8% |  | 53.7998
| Upper quartile efficiency score |  | 82.87%
| Applied efficiency challenge (judgement based on model accuracy) |  | 90%
No. of sites variable was not seen as significant in multiple linear regression model.

## Deep dive_SRN
Deep dive sheet - Southern Water
Summary
Company | SRN
Capex carried through deep dive AMP7 (£m) | 0.44
Ofwat view of allowance for AMP7 (£m) | 0.44
Assessment gates |  |  | References
Need for investment | Pass | The Need for investment is driven by the WINEP programme. However, the driver is listed by the Environment Agency as ‘WATER COMPANY SCALE’ and no site specific requirements are detailed. | (1.) Wholesale Wastewater TA.12. WW06 Business Case - Wastewater Environmental Programme (2.) SRN PR19 Business Plan Data Tables supporting commentary September 2018 (3.) WINEP3 - Environment Agency, March 2018
Need for adjustment | N/A
Management control | N/A
Best option for customers | Partial pass | Southern Water used the Water UK Storm Overflow Assessment Framework (SOAF) methodology to assess the schemes. Solutions include: - 10% reduction in surface water contributing area - 40% reduction in surface water contributing area - Network storage - Infiltration reduction by sewer rehabilitation SUDS were also considered as part of the first two points. | see above
Robustness and efficiency of costs | Partial pass | For the IAP stage we determine costs using the econometric model. Southern Water is an outlier on costs - having a very low unit cost and this appears to be due to a mismatch between costs stated in Table WWS2 and scheme numbers and storage volumes stated in Table WWS4. SRN only claims to have one scheme under the U_IMP4 driver (Ditton Polegate Road) and the associated output of 94m3 claimed in 2024-25 is assumed to relate to the capex of £0.441m spread evenly over 2021-22 and 2022-23. The additional 1,646m3 of storage reported on line 11 in 2021-22 appears to be associated with 3 schemes with shellfish water drivers (Blechynden Terrace Southampton, Ensign Park Hamble, Downes Park Totton) the costs of which (£6.425m according to Appendix 1 of the business case (p70)) are not reported in line 11. (These costs are included in Table WWS2 Line 4 - Conservation drivers.) We therefore exclude this volume from our analysis of U_IMP4 costs. | see above
Customer protection | N/A
Affordability | N/A
Board assurance | N/A

## Deep dive_WSH
Deep dive sheet - Welsh Water
Summary
Company | WSH
Capex carried through deep dive AMP7 (£m) | 48.02
Ofwat view of allowance for AMP7 (£m) | 25.3149
Assessment gates |  |  | References
Need for investment | Pass | Investment driven by WINEP programme. | (1.) WRef 5.8P PR19: Wastewater NEP September 2018
Need for adjustment | N/A
Management control | N/A
Best option for customers | N/A
Robustness and efficiency of costs | Partial pass | The Welsh Water programme consists of work to reduce spills at the Menai Strait for shellfish waters (3,000m3 @ £15.5m) and CSO spill identified under SOAF (£39.501m) (1. - pg. 24) - costs are pre-efficiency. The cost reported in the business plan (post-efficiency) is £48.02m for both programmes. We use these figures to split the costs between Menai Strait (48.02*(15.5/(15.5+39.501))=£13.5m), and the remainder of the programme for which we could not find a cost driver (£34.5m). | see above
Customer protection | N/A
Affordability | N/A
Board assurance | N/A
Further analysis
Information provided by WSH for Menai Strait project used in cost modelling and the derived efficiency applied to the remainder of their programme as the company did not appear to estimate an output that we could use
as a cost driver.

## Allowance
Allowed costs
| Assessor's name | MG
| Peer review (initials, date) | KR 22/01/2019
| BoN code | WWS2004CAS
| Enhancement line | Storage schemes in the network to reduce spill frequency at CSOs
| Control | Wholesale wastewater
Cost allowance for AMP7 (£m)
| Company | Capex in business plan - wholesale wastewater | Capex reallocated out to other lines | Capex reallocated in to this line | Net Capex reallocated in | Capex after reallocations | Modelled allowance | Capex allowed - wholesale wastewater | Proportion of Bioresources | Capex allowed - Bioresources | Capex allowed - network plus
1 | ANH | 8.3663 | 0 | 0 | 0 | 8.3663 | 6.0985 | 6.0985 | 0 | 0 | 6.0985
2 | HDD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | NES | 12.586 | 0 | 0 | 0 | 12.586 | 17.4097 | 12.586 | 0 | 0 | 12.586
4 | NWT | 65.9338 | 0 | 0 | 0 | 65.9338 | 53.2029 | 53.2029 | 0 | 0 | 53.2029
5 | SRN | 0.44 | 0 | 0 | 0 | 0.44 | 0.49811 | 0.44 | 0 | 0 | 0.44
6 | SVE | 30.462 | 0 | 0 | 0 | 30.462 | 33.0823 | 30.462 | 0 | 0 | 30.462
7 | SWB | 36.609 | 0 | 2.013 | 2.013 | 38.622 | 41.0939 | 38.622 | 0 | 0 | 38.622
8 | TMS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | WSH | 48.02 | 0 | 0 | 0 | 48.02 | 25.3149 | 25.3149 | 0 | 0 | 25.3149
10 | WSX | 23.2298 | 0 | 0 | 0 | 23.2298 | 18.0032 | 18.0032 | 0 | 0 | 18.0032
11 | YKY | 60.835 | 0 | 0 | 0 | 60.835 | 53.7998 | 53.7998 | 0 | 0 | 53.7998
| Total | 286.4818 | 0 | 2.013 | 2.013 | 288.4948 | 248.5033 | 238.5293 | 0 | 0 | 238.5293