## Cover
Cover sheet
Raw water deterioration enhancement feeder model
Objective
To assess enhancement capex expenditure submitted by companies in their PR19 business plan submissions for raw water deterioration enhancements.
Approach
We assess these costs using our shallow and deep dive process. In our assessment we look for evidence of Drinking Water Inspectorate support for schemes. We are not able to produce a reliable unit cost model and so we assess costs at a scheme level while recognising the individual nature of schemes. We look for evidence of the scale of flow to be treated and the nature of the treatment.

## Data
Data
£m 2017-18 prices
|  |  | realW3010CAW | realW3026TECAW
Code | Company | Year | Investment to address raw water deterioration (THM, nitrates, Crypto, pesticides, others) - capex | Wholesale water totex
ANH21 | ANH | 2021 | 5.1436 | 498.4777
ANH22 | ANH | 2022 | 15.5414 | 579.182
ANH23 | ANH | 2023 | 2.0927 | 637.0942
ANH24 | ANH | 2024 | 0 | 622.904
ANH25 | ANH | 2025 | 0 | 476.3476
NES21 | NES | 2021 | 0 | 349.522
NES22 | NES | 2022 | 0 | 369.464
NES23 | NES | 2023 | 0 | 361.083
NES24 | NES | 2024 | 0 | 337.652
NES25 | NES | 2025 | 0 | 312.163
NWT21 | NWT | 2021 | 0.059093 | 546.9142
NWT22 | NWT | 2022 | 0.059093 | 511.026
NWT23 | NWT | 2023 | 0.059093 | 491.8832
NWT24 | NWT | 2024 | 0.059093 | 466.2618
NWT25 | NWT | 2025 | 0.059093 | 461.4183
SRN21 | SRN | 2021 | 20.241 | 250.372
SRN22 | SRN | 2022 | 22.072 | 250.609
SRN23 | SRN | 2023 | 10.804 | 233.853
SRN24 | SRN | 2024 | 1.529 | 230.237
SRN25 | SRN | 2025 | 0.765 | 261.533
SVT21 | SVT | 2021 | 0 | 0
SVT22 | SVT | 2022 | 0 | 0
SVT23 | SVT | 2023 | 0 | 0
SVT24 | SVT | 2024 | 0 | 0
SVT25 | SVT | 2025 | 0 | 0
SWT21 | SWT | 2021 | 0 | 0
SWT22 | SWT | 2022 | 0 | 0
SWT23 | SWT | 2023 | 0 | 0
SWT24 | SWT | 2024 | 0 | 0
SWT25 | SWT | 2025 | 0 | 0
SWB21 | SWB | 2021 | 6.319 | 164.926
SWB22 | SWB | 2022 | 9.943 | 179.669
SWB23 | SWB | 2023 | 18.523 | 192.194
SWB24 | SWB | 2024 | 17.398 | 181.702
SWB25 | SWB | 2025 | 11.44 | 175.761
TMS21 | TMS | 2021 | 9.0655 | 1070.0059
TMS22 | TMS | 2022 | 2.9582 | 1195.8227
TMS23 | TMS | 2023 | 0.44939 | 1164.8734
TMS24 | TMS | 2024 | 0 | 1136.5628
TMS25 | TMS | 2025 | 0 | 1090.9391
WSH21 | WSH | 2021 | 0.483 | 329.959
WSH22 | WSH | 2022 | 0.505 | 343.76
WSH23 | WSH | 2023 | 0.137 | 335.885
WSH24 | WSH | 2024 | 0.137 | 322.139
WSH25 | WSH | 2025 | 0.137 | 314.649
WSX21 | WSX | 2021 | 1.2534 | 136.1183
WSX22 | WSX | 2022 | 3.493 | 127.6006
WSX23 | WSX | 2023 | 4.0933 | 146.3737
WSX24 | WSX | 2024 | 1.4118 | 127.4812
WSX25 | WSX | 2025 | 0.10558 | 122.7746
YKY21 | YKY | 2021 | 13.329 | 414.655
YKY22 | YKY | 2022 | 17.021 | 412.077
YKY23 | YKY | 2023 | 13.642 | 420.154
YKY24 | YKY | 2024 | 8.989 | 402.704
YKY25 | YKY | 2025 | 7.156 | 374.833
AFW21 | AFW | 2021 | 0.972 | 294.2158
AFW22 | AFW | 2022 | 2.2167 | 293.2506
AFW23 | AFW | 2023 | 0.49778 | 281.713
AFW24 | AFW | 2024 | 0 | 263.0099
AFW25 | AFW | 2025 | 0 | 236.2718
BRL21 | BRL | 2021 | 0.78 | 90.981
BRL22 | BRL | 2022 | 0.78 | 90.582
BRL23 | BRL | 2023 | 1.24 | 91.372
BRL24 | BRL | 2024 | 0.78 | 91.607
BRL25 | BRL | 2025 | 0.78 | 92.655
BWH21 | BWH | 2021 | 0 | 0
BWH22 | BWH | 2022 | 0 | 0
BWH23 | BWH | 2023 | 0 | 0
BWH24 | BWH | 2024 | 0 | 0
BWH25 | BWH | 2025 | 0 | 0
DVW21 | DVW | 2021 | 0 | 0
DVW22 | DVW | 2022 | 0 | 0
DVW23 | DVW | 2023 | 0 | 0
DVW24 | DVW | 2024 | 0 | 0
DVW25 | DVW | 2025 | 0 | 0
PRT21 | PRT | 2021 | 2.872 | 40.407
PRT22 | PRT | 2022 | 1.186 | 38.175
PRT23 | PRT | 2023 | 0 | 38.858
PRT24 | PRT | 2024 | 1.46 | 51.772
PRT25 | PRT | 2025 | 0.258 | 54.732
SES21 | SES | 2021 | 0 | 52.654
SES22 | SES | 2022 | 0 | 57.352
SES23 | SES | 2023 | 0 | 51.918
SES24 | SES | 2024 | 0 | 46.166
SES25 | SES | 2025 | 0 | 45.219
SEW21 | SEW | 2021 | 2.4285 | 172.162
SEW22 | SEW | 2022 | 2.3848 | 199.673
SEW23 | SEW | 2023 | 2.9194 | 208.291
SEW24 | SEW | 2024 | 4.8819 | 186.222
SEW25 | SEW | 2025 | 4.794 | 194.599
SSC21 | SSC | 2021 | 0.29207 | 112.5274
SSC22 | SSC | 2022 | 2.2165 | 116.2956
SSC23 | SSC | 2023 | 2.2165 | 117.9558
SSC24 | SSC | 2024 | 2.2165 | 94.122
SSC25 | SSC | 2025 | 6.8825 | 97.1282
SVE21 | SVE | 2021 | 4.016 | 575.0657
SVE22 | SVE | 2022 | 7.836 | 631.1286
SVE23 | SVE | 2023 | 10.855 | 643.4347
SVE24 | SVE | 2024 | 7.024 | 635.4116
SVE25 | SVE | 2025 | 4.318 | 630.7635
HDD21 | HDD | 2021 | 0 | 26.8721
HDD22 | HDD | 2022 | 0 | 26.6927
HDD23 | HDD | 2023 | 0 | 26.2036
HDD24 | HDD | 2024 | 0 | 25.617
HDD25 | HDD | 2025 | 0 | 25.9173

## Gates & Shallow dive
Gates and shallow dive sheet - raw water deterioration
The assessor and QA
Assessor's name | RP
Date completed | 2018-10-02
Date of plenary meeting | 2018-11-26
Peer review (initials, date and QA log ref.) | AF 29/01/19
The unit
Unit of pound figures: | £m, 207-18 prices
The enhancement line
Enhancement line BoN code | realW3010CAW
Enhancement line description | Capex Investment to address raw water deterioration (THM, nitrates, Crypto, pesticides, others) | [9 empty] | and measures to address raw water deterioration at sites where we have identified an emerging risk through the Drinking Water Safety Plan process [S6021 P12]
Wholesale level | Wholesale water
Common PC and ODI for Water quality compliance. Target typically set at 0 so no out performance just penalty payment.
Gates
Company | Capex requested by the company AMP7 (£m) | Gate 1. Misallocation | [6 empty] | Gate 2. Need for investment |  |  | Gate 3. Materiality | [5 empty] | Gate 4. Unit cost benchmarking |  | Summary of Gates 1 to 4 |  | Shallow dive
|  | Capex to re-allocate to other line AMP7 (£m) | Description of line to re-allocate capex to | BoN code of line to re-allocate capex to | Capex excluded because is requested by the company via CACs AMP7 (£m) | Capex excluded because is covered by ODIs AMP7 (£m) | Capex to carry through Gate 2 AMP7 (£m) | Evidence and references | Capex excluded because NOT supported by need (regulatory body, customers, etc.) AMP7 (£m) | Capex to carry through Gate 3 AMP7 (£m) | Evidence and references | Company's totex for AMP7 (£m) | Materiality of capex carried through Gate 3 AMP7 (%) | Is the amount material? | Carry the assessment through Gate 4? | Capex to carry through Gate 4 and beyond AMP7 (£m) | Evidence and references | Outlier unit costs? | Evidence and references | Decision of Gates 1 to 4 | Capex to carry through shallow/deep dive AMP7 (£m) | Totex efficiency challenge (%) | Ofwat shallow dive capex allowance AMP7 (£m)
ANH | 22.7777 | 0 |  |  | 0 | 0 | 22.7777 | [Table Commentary p76] identifies spend on line is for nitrate removal. No conflicting CACs identified. Schemes deliver to no other lines PCs identify a performance commitment of full compliance with DWI [BP P175] | 0 | 22.7777 | [Table Commentary P77] Letters of support from DWI identified | 2814.0055 | 0.8094% | Yes | No | 22.7777 | Material |  |  | Deep dive (whole or part) | 22.7777 | 15% | 19.361
NES | 33 |  |  |  |  | 0 | 33 | £33m has been reallocated from resilience line. CRI is a common PC. NES has set a target of 0 therefore there is under performance penalty only, NES applies a deadband to this measure. |  | 33 | No DWI letters of support for schemes. NES states they are subject to RWD in the catchments where works to WTWs are proposed but we find no sample data or further evidence of this. | 1729.884 | 1.908% | Yes | Yes | 33 | Material |  |  | Deep dive (whole or part) | 33 | 0.0265% | 32.9913
NWT | 0.29547 | 0 |  |  | 0 | 0 | 0.29547 | UUW identifies that spend is on its scamp programme [table commentaries P119]. The Capex for catchment management activities is £10.07m [S6007 P55]. UUW identifies schemes that are included in this programme but it is unclear which are allocated to this enhancement line and how the allocation is made. | 0 | 0.29547 | UUW states: and measures to address raw water deterioration at sites where we have identified an emerging risk through the Drinking Water Safety Plan process [S6021 P12]. Customers told us that their priorities were the safety and cleanliness of their drinking water supply,[S6007 P5]. Our 2020-2025 Catchment Management programme is an evolution of previous SCaMP programmes, through which we will deliver projects in partnerships with other organisations in order to secure efficiency. Using partnership delivery routes we will deliver catchment management across 600,000 hectares of catchment land, almost 3 times more than during our previous business plan period., [S6007 P6]. | 2477.5035 | 0.01193% | No | Yes | 0.29547 | Not Material |  | UUW identifies that: Compared to 2015-2020, we will improve our management of 300% more catchment land area, for 13% less Totex cost.[S6007 S6.2 P47] The overall Catchment management programme has a capex of £10.07m [S6007 P55] The programme of work is well described. However it is unclear how the overall programme costs has been allocated across business lines. | Shallow dive (whole or part) | 0.29547 | 0% | 0.29547
SRN | 55.411 | 0 |  |  | 0 | 0 | 55.411 | [TA.11.WN02 p4] identifies spend is for nitrate reduction through blending and treatment options at several sites. No conflicting CACs identified. [TA.06.2]No ODI for removal of nitrates identified but water quality compliance if a common PC and financial ODI | 0 | 55.411 | [TA.11.WN02 p3] DWI have confirmed that they will issue Notices to ensure SRN reduce Nitrate. Customer support indicated. | 1226.604 | 4.517% | Yes | Yes | 55.411 | Material |  |  | Deep dive (whole or part) | 55.411 | 10% | 49.8699
SVT | #N/A | [10 empty] | 0 | [9 empty] | #N/A | #N/A
SWB | 77.232 | 0 |  |  | 22.175 | 0 | 55.057 | There are 2 works that employ Slow Sand Filtration (SSF) treatment technology. - Knapp Mill WTW, 1930, proposed AMP 7, £72.566m - Alderney WTW, 1903, £65.871m (£38.3m AMP7 and £27.56m AMP8). [BP doc Delivering Outcomes…. P48 ] identifies 'compliance with water quality standard' financial ODI with underperformance penalty only. [BP Commentary P264] identifies £22.175m Total = quality element of New WTW schemes [at Knapp Hill & Alderney these are subject to CACs]. CACs give Knapp mill 71.6m Totex, Alderney £38.3m totex 20% =£21.98m ? Deduct higher BP value. Value of remaining identified schemes = £41.448m [from BP Commentary P264 - see deep dive] Sum claimed [Column C] now includes £11.6M originally allocated to catchment mgmt. freeform line [WS2 30] and £2.01m originally to management and General investment freeform line [WS2 26]. | 0 | 55.057 | [BP table Commentary P264] identifies that spend is supported by the DWI - Section 28 notices | 894.252 | 6.157% | Yes | Yes | 55.057 | With £22.2m removed as covered in CACs line remains material |  |  | Deep dive (whole or part) | 55.057 | 0% | 55.057
TMS | 12.4731 |  |  |  | 0 | ? | 12.4731 | Spend is on a crypto scheme at Hornsey [Table commentary P54] Profile is £9.066m 20-21, £2.958m 21-22 & £0.449m 22-23. CRI |  | 12.4731 | Investment needed to reduce number of exceedances of drinking water standards and to comply with regulatory notices. Investment is supported by customers.[Claim Identifier CSD006-WS2-13] No DWI Letters of support found | 5658.2039 | 0.2204% | No | Yes | 12.4731 | Not Material |  | Evidence of Optioneering A number of options were considered and the solutions selected were the most cost effective to meet the drinking water standards [CSD006-WS2-13] No work at Hornsey referenced [in PCD5 N'work + price control] No evidence of scale and scope of work at Hornsey found. Therefore it is not possible to cross check costs | Shallow dive (whole or part) | 12.4731 | 13% | 10.8516
WSH | 10.399 |  |  |  |  | 0 | 10.399 | Sum includes £9m reallocated from resilience - line 14 [Table commentary P16]. This is for the Brecon Beacons mega catchment [BBMC] project. Table commentary identities that spend is for Disinfection by-products R & D [£0.686m] & Disinfection by-products Alaw WTW improvements [£0.713m]. Drinking Water compliance has a target of 0 and so only has an associated underperformance penalty. |  | 10.399 | We have also noted an increase in dissolved organic carbon (DOC) in our raw water. This can lead to an increase of disinfection by-products in our drinking water, which are caused by the reaction of free chlorine with organic content. ............Because of our high number of customer contacts, The DWI issued improvement notices for 32 of our 82 water quality zones during AMP6.[Water N'work BP P44-45] The BBMC project is justified o the basis that the area provides approx. 50% of water abstracted by WSH, Scheme is extension of AMP6 [5.8A Water Resources ]. Drivers identified as increased pesticide use and alignment with Environment Act (wales) 2016. [2.1 WR BP P16], WSH has identified customer support for catchment mgmt. approach [2.1 WR BP P17]. The company states that the BBMC scheme has received the support of NRW, DWI and Welsh Government. [WR BP P25]. | 1646.392 | 0.6316% | No | Yes | 10.399 | Not Material |  | Brecon Beacons Mega Catchment - It is not possible to unit cost BM catchment management schemes, consequent to the diversity of areas and approaches. WSH Has In order to improve our monitoring, and move towards a more predictive approach, we have developed Water Source, our evidence-based, collaborative approach to catchment management [2.1 WR BP P19] This should ensure that spend is targeted. WSH identify that it has completed optioneering for both of the two other smaller schemes. It selects a continuation of the AMP6 approach for both. | Shallow dive (whole or part) | 10.399 | 0% | 10.399
WSX | 10.3571 | 0 |  |  | 0 |  | 10.3571 |  | 0 | 10.3571 | [BP P172] identifies regulatory support from EA Also supported by DWI | 660.3486 | 1.568% | Yes | Yes | 10.3571 | Material |  |  | Deep dive (whole or part) | 10.3571 | 0% | 10.3571
YKY | 60.137 |  |  |  | 0 | 0 | 60.137 | [Appendix 14a P10 Table1] Identifies spend at 6 WTWs on RW and TOC enhancement lines. e.g. Spend at Tophill delivers to both RW and TOC. Retain original line allocations No Related CAC Submitted. The Financial ODI for drinking water compliance failures is penalty only. | 1.668 | 58.469 | [Appendix 14a P10 Table1] Identifies £74.5m spend on TOC and RW lines as submitted in the BP these lines total £77m. No evidence found to justify the remaining £2.2m spend so this is deducted pro rata DWI letters of support. [DWI Letters]. YKY identify that customers prioritise clean wholesome water. [App14a P6] | 2024.423 | 2.888% | Yes | Yes | 58.469 | Material |  |  | Deep dive (whole or part) | 58.469 | 10.35% | 52.4195 | 60.137 | 16.821 | 76.958
AFW | 3.6865 | [5 empty] | 3.6865 | Spend is identified as for Pesticides removal £1.2m & Nitrate Treatment £2.49m [App 6 P320]. Financial ODI with penalty only ODI includes deadband. |  | 3.6865 | No DWI letters of support for RWD found. We find evidence of customer support. The company states 'Supplying High Quality Water you can trust achieved the highest score in the BP acceptability survey' [BP App 3 P46]. Final BP has been tested with customers for acceptability The survey found just over eight in ten (82%) customers considering the plan acceptable...............There was a significant swing away from acceptability when the bill impact including inflation was presented. A clear majority of customers - just over six in ten (62%) - were positive about the bill impacts of this plan[App3 P51] | 1368.4611 | 0.2694% | No | Yes | 3.6865 |  |  | The location and scale of the work proposed is unclear. Expansion of catchment mgmt. to reduce the effect of nitrate Totex £ [BP P66], provision of Nitrate Removal £7.47m capex [BP P80], Our Stort Community........ We will invest in a new nitrate treatment system alongside nitrate pollution investigations and catchment management activities across the community to address the increase in concentration of nitrates in our raw sources. [BP P92 & Stort Community Map]. We find no evidence of the scale and nature of works. We apply a 20% challenge to the proposed spend. | Shallow dive (whole or part) | 2.9492 | 6.071% | 2.7702
BRL | 4.36 |  |  |  | 0 | 0 | 4.36 | No CACs submitted BRL Propose financial ODI with underperformance financial penalty only for water quality compliance. [note the company has customer contact appearance ODI with financial penalty and reward for water quality - appearance but no enhancement spend on line]. |  | 4.36 | Need supported by DWI, customer support for catchment management schemes identified [BP P71] | 457.197 | 0.9536% | Yes | Yes | 4.36 | Material |  |  | Deep dive (whole or part) | 4.36 | 7.196% | 4.0463
DVW | #N/A | [10 empty] | 0 | [9 empty] | #N/A | #N/A
PRT | 5.776 | 0 |  |  | 0 | 0 | 5.776 | No CACs submitted. Financial ODI for CRI [DWI measure] included under performance penalty [BP P 37]. Target is UQ. |  | 5.776 | 3 schemes. 1 with DWI Support, 1 with DWI commend for support, 1 where DWI support is being sought but had not been received when BP issued [03/09/18] [BP table P153] | 223.944 | 2.579% | Yes | Yes | 5.776 | Material |  |  | Deep dive (whole or part) | 5.776 | 0% | 5.776
SES | 0 | [5 empty] | 0 | N.A. No costs to this line |  | 0 |  | 253.309 | 0% |  |  | 0 |  |  |  |  | 0 | 9.141% | 0
SEW | 17.4086 | 0 |  |  | 0 | 0 | 17.4086 | No related CAC, financial ODI for DWI CRI compliance with underperformance penalty only | 0.9 | 16.5086 | "two schemes equate to an investment of £16.5 million and have been supported by the DWI."[BP P117] Deduction made because no reference found to remaining £0.9M spend on this line. | 960.947 | 1.718% | Yes | Yes | 16.5086 | Material |  |  | Deep dive (whole or part) | 16.5086 | 0.8562% | 16.3673
SSC | 13.8241 | 0 |  |  | 0 | 0 | 13.8241 | SSC treatment works investment CAC relates to taste odour colour so no relevant CAC. DWI compliance Risk index [Common PC] includes financial underperformance only |  | 13.8241 | DWI compliance driven. DWI Letter of support for Kinver - Cookley and Commend for support for Ashwood. SSC have identified high customer WTP value for Water safe to drink[ App 03 P45] | 538.029 | 2.569% | Yes | Yes | 13.8241 | Material |  |  | Deep dive (whole or part) | 13.8241 | 6.878% | 12.8733
SVE | 34.049 | 0 |  |  | 0 | 0 | 34.049 | No conflicting CACs identified. PC for DWI CRI compliance has a target of 0 and is reputational only | 0 | 34.049 | [App. A8 p67] identifies DWI support for GW schemes, | 3115.8042 | 1.093% | Yes | Yes | 34.049 | Material |  |  | Deep dive (whole or part) | 34.049 | 0% | 34.049
HDD | 0 | [5 empty] | 0 | N.A. No costs to this line |  | 0 |  | 131.3026 | 0% |  |  | 0 |  |  |  |  | 0 | 0% | 0
#N/A
Good examples of exceptional status
[PURPOSE OF THIS BOX: This box is intended to capture good examples of exceptional status. These examples do not affect the assessment of the claim. They are intended to be used to illustrate good practice as and when needed, e.g. in papers to the board.
Please capture here any evidence of:
- Ambition
- Innovation
- Great customer service
- Resilience
- Symmetrical approach ]

## Deep dive_ANH
Deep dive sheet - Anglian Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | ANH
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 22.7777
Ofwat view of allowance for AMP7 (£m) | 15.4888
Assessment
Assessment gates |  |  | References
Need for investment | Pass | We find DWI letters of support for the following schemes; Wighton WTW, Little Saxham Reservoir, Irby Reservoir and Gayton. The driver for all schemes is nitrate levels. ANH provides evidence of increasing nitrate levels at one of the sites - Wighton [table commentary P77]. The company cites intense storms as a result of climate change identified as potential cause of increased runoff/nitrate. | Table commentary P77- 78 DWI Letters of support
Need for adjustment | N/A
Management control | Pass | Outside of management control driven by increasing nitrates in raw water and water supply regulations compliance. | Table commentary P80
Best option for customers | Pass | Schemes are to ensure compliance with drinking water standards. ANH states that the alternate lower cost option of blending - no longer feasible. The company has an ongoing programme of catchment management but identifies that there will be a lag in this delivering benefit to raw water quality. The company proposes to install ion exchange plants to reduce nitrate levels below PCV for all four schemes. The Irby and Saxham sites are blending points for upstream sources. It will treat blended water. | Table commentary P78
Robustness and efficiency of costs | Fail | ANH has employed Mott Macdonald to assess its cost efficiency. Mott Macdonald identifies ANH to be on average 12% below the industry average, however, this figure is subject to a +/- 15% confidence. [10d P2/P3]. We find no scheme level costs in the BP documents for the projects to address raw water deterioration. If we take the scheme level costs from the DWI letters of support which are Wighton £3.8m, Little Saxham Reservoir £8.9m, Irby Reservoir £27m and Gayton £4.15m. Their total value is £43.85m. We find insufficient evidence of the scope and scale of the works to be undertaken at each site or of scheme. The basis on which the proportion of each scheme is allocated to RWD lacks clarity. ANH should provide a justification to support its cost allocation. We apply 20% challenge to the submitted costs because of a lack of evidence of optioneering and provision of scheme level data. We also apply a further company specific cost efficiency challenge. | BP 10d ANH benchmarking DWI Letters
Customer protection | Pass | Schemes covered by DWI regulation notices
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 18.2221
Apply Efficiency Challenge | 15%

## Deep dive_NES
Deep dive sheet - Northumbrian Water
Summary
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | NES
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 33
Ofwat view of allowance for AMP7 (£m) | 0 |  |  | £7m | £26m
Assessment
Assessment gates |  |  | References | Install new UV treatment at Mosswood WTW to manage Kielder crypto risk | DAF treatment at Layer WTW
Need for investment | Partial pass | We did not find DWI letters of support for these two projects.. NES identifies deterioration in raw water quality at both Kielder and Abberton Storage reservoirs. Requiring crypto removal at Mosswood [Kielder WRZ] and turbidity and algae treatment at Layer [source water from Abberton]. However we find no further evidence to support this as we were unable to access the data referenced in App 3.2. Further evidence is required - for example sample records to demonstrate these issues and DWI letters of support. We also considered the assessment from a resilience perspective - see assessment to the right in blue Failure to invest could subject customers to risk of supply interruptions, or water quality issues. However, NES needs to provide further evidence of its risk assessment of this to demonstrate that now is the time for it to act. | Appendix 3.2 Water resilience | Resilience Need: "Risk due to emerging changes in catchment quality (cryptosporidium) and also potential future restrictions on catchment water sources10) at Derwent IR. This is impacting our ability to maintain water quality regulatory compliance and deployable output from Mosswood WTW which supplies over 100,000 properties;" (Appendix 3.2, water resilience, p8) "Batch 1: Install new treatment capability at Mosswood WTW to manage increasing cryptosporidium risk from raw water sources within Derwent IR and the Kielder transfer system. This investment removes the risks of supply restrictions to customers by allowing us to effectively manage cryptosporidium risk from all source waters at Mosswood WTW" (Appendix 3.2, water resilience, p22) There is a need identified of deteriorating raw water quality, and a consequence to 100,000 properties identified, however, no likelihood assesment is presented. Table 8 also states that the schemes is linked to a DWI scheme (NNE_ESK03 - Springwell SR), however, it is not clear how the schemes are linked. It is not clear that this investment relates to a high consequence low probability occurrence and thus is not clearly resilience investment | Resilience Need: "Risk due to emerging changes in catchment quality (turbidity and algae) at Abberton IR impacting our ability to maintain both water quality regulatory compliance and deployable output from Layer WTW which supplies over 300,000 properties;" [BP P109] "Batch 1: Install a new front end treatment process stream at Layer WTW to address the changes to catchment water quality at Abberton reservoir. This ensures the works can maintain its full deployable output capacity all year and removes the risks of supply restrictions to customers caused by changes in raw water quality" There are issues identified with raw water quality impacting on ability to maintain deployable output and potential impacts on 300,000 properties, however, no likelihood assessment is presented. It is not clear that this investment relates to a high consequence low probability occurrence and thus is not clearly resilience investment
Need for adjustment | N/A
Management control | Pass | Deterioration in raw water quality is largely outside of management control. Catchment management programmes seek to address Raw Water Deterioration (RWD) issues and may be used to reduce or eliminate WTW upgrades. NES has identified a "step change in environmental activities, and to help us meet our ambitious goal to demonstrate leadership in catchment management, ..... agreeing shared objectives with partners for better management of all our catchments. We are also expanding the scale of our catchment management activity to protect raw water.”[BP P98] | BP P98
Best option for customers | Partial pass | We identify that the company has a high level of customer support for its plan. However there is no evidence that alternative options were tested with customers and evidence is based on small sample size. All discretionary enhancements were presented to customers and all water schemes achieved an acceptablility of 82% or higher. This demonstrates strong support from customers, however, two things should be noted: 1) There is limited evidence on what was presented to the customers about the schemes and therefore difficult to judge whether an informed decision was made. 2) A small sample size of customers, only 50 participants. NES themselves caution on the interpretation of this data due to the small samples size. "It was imperative to use a qualitative setting to ensure that complex and lengthy information conveyed meaningfully to customers, however please note that due to this, relatively small sample involved in the quantitative voting results, so caution should be taken with interpretation." | BP P187
Robustness and efficiency of costs | Fail | The enhancement business case states that "Technical options for most schemes were often limited as we needed to address a specific risk, be it lack of water transfer capacity or emerging water quality issues." and "Some schemes did allow for optioneering and we used a whole life cost Totex approach to determine the optimal solution for both the business and our customers" These statements suggest that extensive optioneering was not undertaken on how the risks identified could be mitigating in alternative ways. The schemes presented may be the best options but without the evidence of what alternative options have been considered we cannot be confident that the most efficient option has been selected.
Customer protection | Fail | There are no DWI notices, so there is a risk that the company has no incentive to deliver the schemes it proposes. The drinking water CRI is a common PC. NES has a financial penalty; however, this is subject to a deadband [BP P187].
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 0 | lack of DWI support for schemes - no allowance
Apply Efficiency Challenge | 0.0265%
Further analysis
Further evidence is required to justify the need for an allowance for these projects. Particularly DWI support, evidence of deterioration in water quality, the scale and scope of the projects, optioneering and a build up of costs.
DWI Letters for support were found for a number of schemes:
* Reduce the levels of iron, manganese and aluminium in treated water, related to mains sediment and discolouration in the distribution network. - NNE_ESK2 - £24m - Letter of Support - relates to TOC.
* Construction of new service reservoir at Springwell - NNE_ESK03 Commend for support - Does not relate to water quality.
*reduce the levels of iron and manganese in treated water, supplied via Lartington WTW. - NNE_ESK4 £- 66.85m - Letter of Support New Water Mains, pipeline condition assessment, WTW optimisation to remove Fe, Mn, Al and turbidity, catchment mnmgt.
Conclusion: There is no evidence of DWI support for the work at Layer [Essex & Suffolk area] Although Lartington can use similar raw water to Mosswod, the work at Lartington is driven by Taste Odour Colour not Crypto/ Raw water deterioration. No evidence of DWI support for these schemes has been found.

## Deep dive_SRN
Deep dive sheet - Southern Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | SRN
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 49.8699
Ofwat view of allowance for AMP7 (£m) | 49.8708
Assessment |  |  |  | Schemes by size and Totex - Source TA.11.WN02 Appendix 1
Assessment gates |  |  | References | Source | Area | Solution | DWI provisional date | Source Yield, Dry Year Critical Period (DYCP) | Scheme totex |  | Capex from Options Summary Appendix 3 |  | Summary Description of work from DWI letter of support
Need for investment | Pass | SRN proposes an extensive programme of work to address raw water deterioration. These Investments are supported by DWI letters of support and is required to achieve compliance with DW standards. SRN also produce evidence of forecast increasing nitrate levels at a number of sources. SRN has also received DWI letter of support for a number of catchment management schemes. Catchment management is often used to mitigate the need for more costly options. | DWI Letters of Support TA11.WN02 App. 2 |  |  |  |  | (Ml/d) | (£m) | Solution |  | Ofwat Comment
Need for adjustment | N/A |  |  | Timsbury | Hampshire South | Investigation into use of remote sources for raw blending | 2022-12-01 | 10.8 | 1.3 | Blend | 1.5 |  | The current proposal is to re-use a previously abandoned borehole on site. However there is currently insufficient evidence to support this proposal at present. The company are therefore required to complete investigations into the suitable mitigation for Nitrate at this site. - Estimated capital costs: £1.5m (current preferred solution)
Management control | Pass | Nitrate in raw waters is largely as a result of historical practices this is outside of management control. |  | Easton | Hampshire South | Continue monitoring – no investment required | N/A |  |  |  | 0
Best option for customers | Pass | SRN have consulted customers to identify a WTP for DW compliance of £1.37 [P20]. SRN identify a number of options: Do nothing & catchment management [time lag between implementation and benefit, blending [P88] are discounted because of risk of non compliance with DWI. The selected options are mixture of blending and/or treatment. The selected treatment option is Ion exchange The ion exchange plants we installed during AMP6 proved to be a suitable, cost-effective process to remove nitrate. We are also considering innovative solutions such as biological removal. The costs in this technical annex related to ion exchange treatment.[TA11.WN02] Selection between treatment or blending is evidenced by concentration prediction trends [P23 -P26]. | TA11.WN02 P4 - page refs in assessment | Twyford | Hampshire South | Treated water blending | 2021-12-01 | 23 | 2 | Blend | 2.2 |  | Nitrate - Provision of increased blending and monitoring facilities at Twyford treatment works to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £2.2m
Robustness and efficiency of costs | Partial pass | TThe company provides a schedule of selected options with plant sizes and costs [App1]. as well as Capex and Totex and split of costs between base and enhancement [Table3]. We note that £20.371m [approximately 25%] of the scheme level costs is allocated to base. However, we find no methodology or detail of how this split is determined. We note there is some inconsistency between totals derived from data in TA.WN02.Table 3 and also when compared to Appendix 3. SRN identifies that its cost estimation process has been independently reviewed by Jacobs [TA14.4 P8] . “for example, a cost curve for a nitrate removal plant will be based on many different equipment sets that make up the nitrate removal plant function, such as: pumps, valves, pipe lines, sampling equipment, instrumentation, nitrate removal treatment etc. The function curves were developed based on actual SWS sites, supported through the blending of historically captured cost data points.”[TA 14.4 P14] SRN commissioned Mott Macdonald to benchmark and validate net direct costs “benchmarking work confirmed that the pre efficiency capex costs going into the plan are deemed to be at median to upper quartile levels of delivery efficiency. We have adjusted our costs downwards to target the level of efficient costs.”[TA 14.4 P18] Mott Mac Report not located. SRN has also benchmarked indirect cost multipliers against water industry peers and road rail etc. “told us that the pre efficiency multipliers being used to cost our PR19 capital schemes are at median to upper quartile levels of delivery efficiency. We have adjusted our costs downwards to target the level of efficient costs”.[TA 14.4 P19] We can find no examples of this benchmarking. Summary: SRN identifies scheme level costs and capacities of WTWs where work is to be completed. SRN identifies that a proportion of work is to be charged to RWD. SRN has produced costed options for each scheme. Scheme costs allocated to RWD appear reasonable, however, further evidence to demonstrate how the cost split has been calculated should be provided. | TA11.WN02 App1 and Table3 TA14.4 | Patching | Worthing | Raw water blending | 2022-12-01 | 2 | 3.7 | Blend | 5.6 |  | Nitrate - Provision of blending at Patching treatment works to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £5.6m
Customer protection | Partial pass | Customers are protected by DWI letters with required completion dates. SRN identifies the opportunity that it might be able to defer some spend to AMP8 if nitrate increases at a rate lower than predicted. No evidence found as to how customers would be protected in this case. | DWI Letters of Support TA11.WN02 App. 2 | Madehurst | Worthing | Continue monitoring and turn off source during periods of high nitrate – no investment required | 2025-12-01 |  |  |  | 0 |  | Madehurst – Nitrate - Provision of raw water blending of the Clapham, Angmering and Patching sources at Patching to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £0.5m
Affordability | N/A |  |  | Beacon Lane | Thanet Mid | Raw water blending then treatment at Flemings site | 2025-12-01 | 4.5 | 8.3 | treat | 0.11 |  | Nitrate - Provision of treatment facilities at Wingham and Flemings with Beacon Lane raw water imported to Flemings and a new main to send Flemings and Beacon Lane water to Wingham to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £42.6m NPV
Board assurance | N/A |  |  | Flemings | Thanet Mid |  |  |  |  | treat | 7.76
|  |  |  | Wingham | Thanet Mid | Treatment | 2025-12-01 | 13.1 | 7.2 | treat | 7.085
|  |  |  | Sparrow Castle | Thanet North | Raw water blending then treatment at new works – Thanet North | 2022-12-01 | 6.5 | 15.5 | blend | 2.1 |  | Nitrate - Provision of treatment facilities at Minster and raw water imports/blending from Lord of the Manor and Sparrow Castle to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £20.29m
|  |  |  | Minster B | Thanet North |  |  |  |  | treat | 13.257
|  |  |  | Deal Low | Thanet South | Raw water blending then treatment at Sutton | 2022-12-01 | 9 | 13.4 | blend | 3.225 |  | Nitrate - Provision of treatment facilities at Sutton and raw water transfer from Deal to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £15.73m
|  |  |  | Sutton | Thanet South |  |  |  |  | treat | 13.195
|  |  |  | London Rd Strood | Medway | Maintain existing treated water blending arrangements – no investment required | N/A |  |  |  | 0 |  | Nitrate and sufficiency - Design the provision of treatment facilities at Patcham, return the Surrenden source to supply and install the treatment facilities once required to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £10.4 NPV Identified as zero cost - blending sufficient in SRN BP documents
|  |  |  | Newmarket B | Brighton East |  |  | 17.7 | 28.3 | blend | 21.265 | Scheme Description from TA.11.WN02 App. £ options summary: Convert to UGS and transfer to new Brighton East WSW to be treated with Housedean. Conclusion costs are for transfer to address RWD only | Brighton New Works - Nitrate - Provision of a new treatment works to replace Housedean, Newmarket B, Newmarket C, Newmarket D and Falmer treatment works, to secure or facilitate compliance with the Nitrate standard - Estimated capital costs: £115m npv
|  |  |  | Newmarket C/D | Brighton East |  |  |  |  | blend | 1.4 | Housedean Selected option is blend and transfer to new WTW
|  |  |  | Totals |  |  |  | 86.6 | 79.7 |  | 78.697
SRN have also provided data to split cost TA.11.WN02 Table 3 P15 Data from Table 3. below
|  |  |  | Capex for schemes TA.!!.WN02. Table 3 |  |  |  |  | 75.783
|  |  |  | Overall % Capex of totex |  |  |  |  | 95.09%
|  |  |  | Capex charged to Enhancement Line |  |  |  |  | 55.412
|  |  |  | Capex charged to Base [TA11.WN02. Table 3 |  |  |  |  | 20.371
|  |  |  | Proportion of project Capex allocated to base |  |  |  |  | 26.88%
Allowable costs [from submission] | 55.412
Apply Efficiency Challenge | 10%
Further analysis
[BP Table Commentary P63] identifies achieving compliance with nitrate standards is the reasons for spend allocated to this line [Wholesale Water TA.11.WN02 Business Case - Nitrate.] There are a number of DWI letters of support and these have been mapped to the schemes proposed by SRN - see column J- U of this worksheet.
The scheme names from the DWI letters are: * Brighton New Works - Nitrate, * Brighton Patcham – Nitrate and sufficiency , * Twyford - Nitrate , * Mid Thanet - Nitrate , * North Thanet - Nitrate ,* South Thanet - Nitrate ,* Timsbury, * Worthing Madehurst – Nitrate, *Patching - Nitrate.

## Deep dive_SVE
Deep dive sheet - Severn Trent Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | SVE
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 34.049
Ofwat view of allowance for AMP7 (£m) | 21.8116
Assessment
Assessment gates |  |  | References | Schedule of schemes - data from App A8 P71 and DWI letters for scheme level cost data.
Need for investment | Partial pass | SVE identifies the limitations of catchment management as an option [App A8 ]. SVE provides evidence that options including abandonment have been considered. The UV treatment is justified: “The AMP7 programme of nine UV disinfection plants...... deliver our strategy of moving away from marginal disinfection, as has been the industry approach.”[App A8 P67]. We did not find evidence to demonstrate deterioration in compliance with DWI standards, particularly for sites without full DWI support. SVE provides some evidence of optioneering, but a more detailed assessment e.g. comparison of costed options would support option selection. | Appendix 8 DWI letters | Works | Output [Ml/d] | Scheme Cost from DWI Letters of support | Work Category | Primary Removal Objective of Process | Description of work | DWI Support
Need for adjustment | N/A |  |  | Coopers Green WTW |  | 8.55 | Treat | As | Installation of enhanced treatment facilities at Peckforton source to treat water from Peckforton, Tower Wood and Tattenhall borehole - Arsenic removal | DWI Letter of Support
Management control | Pass | Raw water deterioration is largely outside management control. |  | Overton Scar |  |  | Blend | As | No cost estimate included with the DWI letter Arsenic | DWI Commend for Support
Best option for customers | Partial pass | SVE identifies the limitations of catchment management as an option [App A8 ]. SVE provides evidence that options including abandonment have been considered. The UV treatment is justified: “The AMP7 programme of nine UV disinfection plants...... deliver our strategy of moving away from marginal disinfection, as has been the industry approach.”[App A8 P67]. We did not find evidence to demonstrate deterioration in compliance with DWI standards, particularly for sites without full DWI support. SVE provides some evidence of optioneering, but a more detailed assessment e.g. comparison of costed options would support option selection. | App A8 P67-69 | Chaddesley Corbett |  | 3.8 | Blend | Se | Blending by bringing additional water in to Mustow Green DSR from a main which is fed by a combination of the Green Street and Blackstone groundwater sources. Both Green Street and Blackstone are low (<0.5 μg/l) selenium sources. Selenium concentration reduction | DWI Letter of Support
Robustness and efficiency of costs | Partial pass | SVE provides evidence of third party review of its costs. Both at item level and of general recurring project costs. SVE proposes UV treatment at many of the sites. The company states:” Our vision is to outperform our efficiency challenge and to do this through a Factory Thinking approach....... To do this we challenged standards and sought productive efficiencies through batching and planning”...... We have also significantly increased the use of factory built assemblies and sought collaborative and coordinated delivery across tier 1 and tier 2 suppliers.[SVE App A8 P70]. However, we find no further evidence to support this. Summary: We find no scheme level cost estimates or information as to treatment works flows in the business plan submission. We make no allowance for the schemes where we find no evidence of DWI support. We take scheme level cost data from DWI letters of support to which we apply a 20% challenge due to lack of sufficient information about the schemes for us to be confident that they are value for money. Our scheme level analysis is included in columns I to P. | BP Section 20.3 P223 on DWI letters Appendix 8 | Beckbury WTW |  | 1.7635 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
Customer protection | Pass | Customers are protected by DWI notices issued with letters of support for some of the schemes. Failure to achieve CRI performance commitment will result in reputational damage. |  | Bratch WTW |  | 1.0751 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
Affordability | N/A |  |  | Brockhill WTW |  | 0.74086 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
Board assurance | N/A |  |  | Budby WTW |  | 0.81024 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
|  |  |  | Clipstone WTW |  | 0.8619 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
|  |  |  | Grindleforge WTW |  | 0.81795 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
|  |  |  | Oakley Farm WTW |  | 0.66395 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
|  |  |  | Puleston Bridge WTW |  | 0.59512 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
|  |  |  | Tack Lane WTW |  | 1.0398 | UV | Pathogens | UV treatment and catchment management. - Pathogens | DWI Letter of Support
|  |  |  | Epperstone WTW |  |  | Blend | Nitrate | blending solution Nitrate DWI final decision letter 30 May 2018 did NOT support - insufficient justification of need for drinking water reasons estimated Totex £3.8m | DWI letter NOT SUPPORTED
|  |  |  | Newent WTW |  |  | Blend | Nitrate | blending solution Nitrate DWI final decision letter 30 May 2018 did NOT support insufficient evidence of genuine risk - Totex £4.14m | DWI letter NOT SUPPORTED
|  |  |  | Hatton WTW |  | 6.5461 | RO |  | Installation of Reverse Osmosis treatment at Hatton WTW in order to ensure the compliance with the Taste and Odour standard further research and development would be required to establish suitability of an Ion exchange process for the removal of the Sodium and Chloride believed to be causing taste and odour failures [App A8 P69] | DWI Letter of Support
[5 empty] | Total schemes with DWI support/commend | 27.2646
[5 empty] | Totex for not supported | 7.94 | Epperstone and Newent [Costs from DWI decision letters]
[5 empty] | % of scheme level costs passed | 0.8
[5 empty] | Total allowed | 21.8116
Allowable costs [from submission] | 21.8116
Apply Efficiency Challenge | 0%
Further analysis
Schemes are scheduled on this deep Dive Analysis tab. No evidence of the DO from each WTW found. DWI Support or commend for support found for all schemes except for Newent and Epperstone which the DWI do not support. No further evidence to explain drivers for Overton Scar [DWI commend for support] found

## Deep dive_SWB
Deep dive sheet - South West Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 29/01/19
Company | SWB
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 55.057
Ofwat view of allowance for AMP7 (£m) | 41.5544
Assessment gates |  |  | References
Need for investment | Pass | The company’s need for investment is evidenced by DWI section 28 Notices and DWI letters of support for schemes at the following water treatment works: Restormel, Prewley, St Cleer, Stithians, Littlehampton, Knapp Mill & Aldernery. SWB submitted a cost adjustment claim for the work at Knapp Mill and Aldernery, and we assess the costs for this within the cost adjustment claim. In addition we reallocate two further programmes to this enhancement line: Upstream Thinking project for catchment management work, originally submitted as a freeform enhancement line. This has received DWI 'Commend for support'. We also add to the costs we review here part of the Management and General Investment freeform enhancement line expenditure. The value reallocated to this enhancement line is £2.01m. This programme of work has received DWI support this justifies the need for investment. However, evidence of deterioration in raw water for example time based trends to evidence Manganese, bacterial, DOC etc. would further support the case. | DWI Letters of support, Upstream thinking DWI commend for support BP commentary
Need for adjustment | N/A
Management control | Pass | Presence of Manganese, bacteria and DOCs in raw water sources is largely outside of management control.
Best option for customers | Partial pass | SWB has implemented catchment mgmt. since 2004. In regard to this work SWB states “Our programme delivers right to the heart of the Government 25 Year Environment Plan with wider ecosystem benefits. The total natural capital value delivered by the Investment was found to be in excess of £40m over the period 2020-45, assuming 2015-20 investment levels are continued........ This is approximately a 1:3 return on the investment. This means customers are getting more for their money than they would from traditional end of pipe solutions”, [WR Wholesale Rev. P26]. The approach is appropriate. SWB identifies that it considers the benefits from catchment management when scoping upgrade / replacement of treatment processes required to address raw water deterioration issues. It states: “We will ensure these improvements use modern efficient and sustainable solutions, sized to reflect anticipated raw water quality improvements from our catchment management work, thus keeping costs to customers as low as possible.” [Nwork + Water wholesale control P80 ] However, we find insufficient evidence that the company has fully evaluated all options for resolving the issues of raw water deterioration. | Network and Water Wholesale Control Water Resources Wholesale Revenue Control.
Robustness and efficiency of costs | Partial pass | There are 2 programmes of work. Catchment Management "Upstream Thinking" - £11.6m and WTWs upgrade £41.6m. In addition £2.1m originally identified as 'for management and general investment.' is reallocated to this line. Catchment Management: BP documents estimate benefits from the programme as similar those for 2015-20. We assume similar levels of cost to deliver these benefits. The proposed programme total for 2020-2025is £16.9m and the spend for 2015-2020 is £10.5m. To set the allowance we apply the CPIH increase from 2012-13 to 2017-18 of 1.07895 to the AMP6 spend of £10.5m to give £11.329m programme value for 2020-2025. We note that SWB allocates the 2020-2025 programme to two enhancement lines freeform [68.8% of programme costs] and drinking water protected areas [31.2% of cost]. We apply this split to the our assessment to give an allowance of £11.329m * 68.8%= £7.796m. Schemes at WTWs: We find Scheme level cost data in the DWI letters of support, but no further scheme level data in the BP. Allowed costs have been built up from scheme level data for Restormel, Prewley, St Cleer, Stithians, Littlehampton, Knapp Mill & Aldernery. As we find insufficient evidence of costs or optioneering, we apply a 20% challenge to WTW scheme costs = £40.22*0.8 =£32.18m. We assess the costs for Aldernery and Knapp Mill under the cost adjustment claim. SWB proposed to allocate £22.2m of the costs of these schemes to raw water deterioration enhancement. . General Management: £2.01m is transferred to this line from the management and general investment freeform line. Using WTW scheme level data we find evidence of £76m that is allocated to this line. This includes enhancement for 2020-25 at Aldernery and Knapp Mill. We disallow £0.122m of the £2.01m. This is the proportion of the general management which relates to the original line allocation for which we find no evidence i.e. (£77-£76m)/£77m * £2.01m. As we find insufficient evidence of costs of optioneering of the schemes we apply a 20% challenge to the remainder to give an allowance for management of these schemes of £1.582m. Our total allowance comprises catchment management £7.796m, 5 schemes at WTWs £32.18m and general management £1.582m. SWB report demonstrates its approach costing: “We engaged industry experts, Chandlers KBS and Aqua Consultants, to undertake a review of our cost models and data compared to peers within the industry. They concluded that, based on the comparative information available, South West Water models are competitive with a good indication that the models are efficient and with limited scope for further efficiencies at the business planning stage”.[Securing cost efficiency P31] We did not find the Independent Report; inclusion of independent reports would support claims for cost efficiency. | BP Table commentary PBP Securing Cost Efficiency P31
Customer protection | Pass | Customers are protected by DWI notices issued with letters of support for all 5 sites. The company also proposes a financial ODI. | DWI Support Letters BP P50
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 41.5544
Apply Efficiency Challenge | 0%

## Deep dive_WSX
Deep dive sheet - Wessex Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | WSX
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 10.3571
Ofwat view of allowance for AMP7 (£m) | 8
Assessment
Assessment gates |  |  | References
Need for investment | Pass | The company proposes two schemes relating to raw water deterioration. In relation to Sturminster Marshall and Fonthill Bishop the DWI states:” The Inspectorate has formally supported all of the Company’s proposals and we will put legal instruments in place to make the proposals legally binding programmes of work........ The remaining schemes are for blending in distribution to mitigate increasing levels of nitrate in raw water to 2 groundwater sites.”[DWI inspectorate Statement App. 5.3.D ]. WSX states “Three groundwater sites (Deans Farm, Fonthill Bishop and Sturminster Marshall & Shapwick) have had catchment management implemented over the last 10 years with the aim to keep nitrate levels below the DWI standard. Over the last couple of years there have been increased failures of this standard, with a rising trend and increased peaks of nitrate.....scheme has been successful in delaying capital expenditure by over 10 years.”.[supporting doc 3.3 P154] nitrate trend data is provided [supporting doc 5.3.A.2 Annex 1 and 2] The need for investment is evidenced by DWI letters for support and limitations in the current catchment management programme. | DWI inspectorate Statement in App 5.3.D P4. DWI letters of support. Supporting Doc. 3.3 Supporting Doc 5.3.A.2 Annex 1 and 2 Nitrate schemes
Need for adjustment | N/A
Management control | Pass | Nitrates in ground water are very largely outside of management control, and we recognise that the company’s catchment management programme has delayed the need for this expenditure.
Best option for customers | Pass | WSX provides evidence of cost benefit analysis [S. Doc 3.3 P154 on]. The selected option does not have the best cost benefit but avoids reduced deployable output which would be the result of the lowest cost benefit option. We accept this evidence. Optioneering has been completed. WSX identifies that its proposed blending option is lower cost than treatment at Fonthill [S. Doc 5.3.A02.Annex 1 P23] For Sturminster WSX identifies that blending is lower cost than treatment on site, source abandonment is discounted on resilience grounds [S. Doc. 5.3.A.2 Annex 2 P54] | Supporting Doc. 3.3 Supporting Doc 5.3.A.2 Annex 1 and 2 Nitrate schemes
Robustness and efficiency of costs | Partial pass | WSX outlines its approach to estimating efficient costs “We break each project down into its constituent parts and build bottom-up estimates. ...... Every project is then reviewed technically and financially as part of our financial governance processes before the project can proceed to contract award and delivery. Projects greater than £2m in value require approval by the board” [BP P217]. However, we can find no evidence of bottom up cost estimates or cost build up of the schemes.. ThereforeWSX provides insufficient evidence of costs estimating. Scheme level capex costs of £6-8m for Fonthlll Bishop [S. Doc 5.3.A02.Annex 1 P23] and £2m for Sturminster [S. Doc. 5.3.A.2 Annex 2 P54]. The same Capex values are presented in the DWI letters of support. Summary: We make allowance using the lower cost estimate for Fonthill Bishop and the cost estimate for Shapwick/Sturminster. Further separation of costs elements [for example between pipeline and blending at Fonthill] and scale of flows to be treated would allow us to make an improved assessment. | BP P217 Supporting Doc 5.3.A.2 Annex 1 and 2 Nitrate schemes
Customer protection | Pass | Customers are protected by DWI notices issued with letters of support for all sites. WSX also proposes a financial ODI. | DWI letters of support
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 8
Apply Efficiency Challenge | 0%
Further analysis
The following scheme descriptions have been taken from the DWI letters of support:
* Fonthill Bishop - Nitrate Blending - Blending- conversion of the existing system from Fonthill to Littledown into a dedicated high nitrate pipeline for blending at Littledown SR and utilisation within regional grid. The scope of works will be: 6km of 400mm diameter pipeline, major connection detail at East Knoyle and blending arrangement at Littledown including relocation of disinfection from Fonthill.
* Shapwick / Sturminster Marshal- Nitrate - To construct upgraded blending facilities at Sturminster Marshall. The anticipated works include:
~ Washout improvements at Shapwick to enable each borehole to be washed out independently
~ A static mixer to enable the Shapwick/Sturminster flows to be blended in a controlled manner with the inflow from Black Lane
~ A pump on the outlet of Sturminster Marshall contact tank to enable the two sources to be blended through the static mixed.
~ Increased nitrate monitoring and control facilities.

## Deep dive_YKY
Deep dive sheet - Yorkshire Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | YKY
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 58.469
Ofwat view of allowance for AMP7 (£m) | 35.9241
Assessment
Assessment gates |  |  | References
Need for investment | Pass | We find DWI letters of support for all projects allocated to this line. YKY demonstrates increasing trends in Nitrate and herbicide levels and maps risks for these and Cryptosporidium to its RW sources [App 14a - P22 -P25]. YKY provide evidence of crypto. in raw water at Tophill Low [App14a Pt. B P16] and increasing trends in raw water colour at other WTWs [App14a Pt. B]. The company demonstrates a range of catchment management projects are used to reduce spend [App 14A P29 - P31]. The need for investment is well evidenced. | DWI Letters of support. App14a | Data from YKY App14a >>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>>
Need for adjustment | N/A |  |  | Works | Output [Ml/d] | Capex | Calculated Unit Cost /Ml/d | Description of work | Comment | Ofwat Assessment | Cost Allowance
Management control | Pass | Raw water quality is largely outside of management control. |  | Chellow Heights | 175 | 23.9 | 0.13657 | 100Ml/d I-Ex / PAC refurb /chemical dosing / run to waste |  | Chellow - lowest Whole Life Cost solution not selected- deduct 10% | 21.51
Best option for customers | Partial pass | Yorkshire Water is continuing to develop catchment management options - as these also manage raw water deterioration risk. Chellow Heights Pass - YKY has discounted lower whole life cost options because they were less likely to resolve risk. [App 14A Pt B P31-32] Oldfield /Sladen Valley Fail . YKY considers a number of options for these two sites - including combining the two sites. Costs of all options are not presented. [App14a. Pt B P41 43]. In discounting combining the works YKY states that Sladen Valley is a more modern WTW and would generate significant write-off costs were it to be closed.[App14a pt. P43] but it also states Sladen Valley WTW is an ageing asset,[App14a Pt. B P44] YKY also identifies that combining the works is the lowest whole life cost but creates a new resilience risk. [App14A Pt. B P52]. We find insufficient evidence to support this. The option for combining treatment at a single site proposes ion exchange but for only 50% flow [App14a Pt B P51] whereas the independent schemes propose ion exchange for 100% of flow at each site. This appears inconsistent without explaining the blending options available. Fixby Pass - YKY identifies lowest whole life cost option is selected but costs of alternate not provided. Tophill Low Pass - now allocated 50% to raw water deterioraton. YKY have discounted lower whole life cost options because they were less likely to resolve risk. [App 14A Pt B P72] Summary: Further evidence of costings and consideration of resilience risks should be provided for Oldfield /Sladen Valley | App14a Pt. B | Oldfield | 12 | 6.1 | 0.50833 | DOC I-Ex / 3 stage rebuild / enhanced Run to Waste | In addition, the scheme also incorporates significant base-maintenance investment to improve the overall resilience of the site, and aid recovery from failure. Site is uprated from 10 to 12 Ml/d | Oldfield YKY advise scheme includes base mtce and investment to improve site resilience Base maintenance is not enhancement a deduction of 20% is made. | 4.88
Robustness and efficiency of costs | Fail | YKY states “We have identified six water treatment works where significant process enhancement is required to guarantee the quality of drinking water in the face of raw water deterioration. However, alongside this enhancement Yorkshire Water PR19 Submission investment there is a significant element of enabling base maintenance required.......This has been allocated to base maintenance as per the regulatory accounting guidelines.” [App8f P18]. We find that the proposed spend on raw water deterioration and taste odour colour enhancement lines = sum of preferred option costs from App14a. We find no evidence of parts of spend being allocated to base. We could find no evidence of third party assurance of cost estimates. Yorkshire Water aims to deliver 14% efficiency improvement over its costs for the 2015 to 2020 period [BP P56]. We provide our analysis scheme level analysis in columns J to Q of this worksheet. Summary: YKY provides scheme level cost data [App 14a] and flow capacities of several WTWs with schemes.. We consider that part of the cost of schemes should be allocated to base maintenance, however, we find no evidence that the company has done this. Where schemes include refurbishment or work to replace deteriorated or substandard assets or the company is not selecting the lowest whole life cost options, we apply cost challenges at scheme level. Allowed cost has been built up from scheme level data * Chellow - lowest Whole Life Cost solution not selected- deduct 10% * Oldfield YKY advise scheme includes base maintenance investment to improve site resilience - Deduct 20% * Sladen Valley - scope appears similar to Oldfield & includes bas maintenance investment - as no evidence found for differences in costs, accept similar cost to Oldfield * Fixby scheme includes refurb elements accept 50% of costs * Embsay includes contact tank replacement this is regarded as base maintenance and we allow 75% of costs. Total spend we allow before any efficiency challenge is £40.07m | App8F App14a App 14a Pt. B | Sladen Valley | 12 | 14.6 | 1.2167 | DOC I-Ex | In addition, the scheme also incorporates significant base-maintenance investment to improve the overall resilience of the site, and aid recovery from failure. | This project appears similar in scope and scale to Oldfield but costs are over double. No clear evidence has been found to justify the increased cost. Accept cost from Oldfield | 4.88
Customer protection | Pass | Customers are protected by DWI notices issued with letters of support for all sites. YKY also proposes ODI penalty to protect customers from non-delivery. |  | Fixby | 30 | 5.6 | 0.18667 | DAF refurb / Additional RGF | Fixby output would be increased this could improve resilience. | RW deterioration £5.6m but scheme is described as refurbishment, this is a base cost. Also no evidence of costs of alternate option have been found A deduction of 20% is applied for lack of evidence of optioneering. A further deduction is made because refurbishment is base maintenance. A total 50% deduction has been applied in respect of both. | 2.8
Affordability | N/A |  |  | Embsay | 24 [typically 18] | 8 | 0.33333 | Mn Contactors and new contact tank run to waste | Contact Tank life expired - Base, YKY are targeting reductions in ex works Mn to reduce customer contacts [i.e. TOC Complaints] | Mn is usually associated with TOC however in this case change in RW drives change in Mn removal process to ensure treated water compliance. This Scheme includes contact tank replacement which is considered to be base maintenance - £2m [ 25% of scheme costs] the estimated cost of contact tank replacement. | 6
Board assurance | N/A
|  |  |  | Total RWD |  | 58.2 |  |  |  | RWD Enhancement Spend Allowance | 40.07
Allowable costs [from submission] | 40.07
Apply Efficiency Challenge | 10.35%
Further analysis
YKY proposes work at an number of WTW all of which are supported by the DWI . Summary details taken from DWI letters is :
* Chellow Heights - DBP’s - Provision of treatment facilities at Chellow Heights WTW to reduce the formation of DBP’s - Total cost £23.9 M capex
* Embsay- DBP’s and Cryptosporidium - Provision of treatment facilities at Embsay WTW to reduce the formation of DBP’s and reduce the risk of Cryptosporidium Estimated Capex £8m
* Fixby - DBP’s - Provision of treatment facilities at Fixby WTW to reduce the formation of DBP’s -Total cost £5.6 M capex
* Oldfield - DBP’s - Provision of treatment facilities at Oldfield WTW to reduce the formation of DBP’s -Total cost £6.1 M capex
* Sladen Valley - DBP’s - Provision of treatment facilities at Sladen Valley WTW to reduce the formation of DBP’s -Total cost £14.6 M capex .
In addition to the above YKY also has a letter of support for
* Tophill Low- Taste, Odour (T&O) and Cryptosporidium - Provision of treatment facilities at Tophill Low WTW to secure compliance with the Taste and Odour drinking water quality standards, and to reduce the risk of Cryptosporidium - Estimated Capex - £16.3m - Although the need for investment at Tophill is similar to that for Embsay YKY has elected to allocate work at Tophill to Taste Odour Colour. We have retained YKY's allocation.
Summary: YKY presents evidence that these WTWs are subject to RW deterioration and also records of Taste, odour anc colour complaints in related supply areas. Options have been considered and proposed work at the WTWs will address both RW and TOC issues. Evidence of consideration of part flow options should be provided. Also some of these schemes will replace deteriorating assists replacement work is considered to be base expenditure.
There is limited information on costs of non preferred options and limited evidence of assurance of cost efficiency.
A high level cost comparison of the schemes identifies considerable variation in unit costs - for example comparison of the Oldfield and Sladen Valley schemes. Further detail on the cost estimates enables better comparison and identification of base cost elements..

## Deep dive_BRL
Deep dive sheet - Bristol Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | BRL
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 4.36
Ofwat view of allowance for AMP7 (£m) | 0.4269
Assessment gates |  |  | References
Need for investment | Pass | We find a DWI letter of support for the proposed work for improving processes at Cheddar WTW. | DWI Letter of Support
Need for adjustment | N/A
Management control | Pass | Deterioration of raw water is largely outside of management control. However BRL are also implementing catchment management schemes to mitigate effects.
Best option for customers | Pass | BRL states “We have proposed to the DWI that the PR19 Notice associated with Cheddar should be amended to an extension of the existing BRL 3506 Notice, which details investigations to be undertaken to determine the most appropriate solution. We accept that this could lead to an increased risk of enforcement to undertake remedial measures during AMP7..... We have taken this into account in our financial viability testing. However, we feel this risk would be outweighed by the extra confidence we would gain by ensuring any treatment related option would be the optimum solution for the risks associated with the deteriorating raw water quality. This way, customers do not pay in advance of us being confident that the right option for the long-term has been selected, without any risk to their supplies.”[Section A1 P60]. We accept this approach. BRL identifies options for the schemes [C5b.TA15 App D. Table] A number of options are identified but only one of which is discounted as unviable. Only the costs of the selected option is presented, other options are not costed. The extended trials option is selected based on DWI support. | Bristol Water For All' Section A1 P60 BRL.C5B.Technical Annex 15 Treatment Works Strategic Maintenance Appendix D
Robustness and efficiency of costs | Partial pass | BBP table WS2.13 identifies cost of £4.36m for raw water deterioration all on water resources. The DWI letter identifies covering of the slow sand filters at Cheddar to limit algal growth in the filter at a cost of £4.2 -£4.7m. Within its business plan documents [BP Annex 15 P29 Table 8 Selected interventions] Bristol Water identifies a budget of £0.5m for Cheddar. The other schemes proposed in Annex 15 are base maintenance BRL identifies that it is applying a capex efficiency challenge of 8% to the Cheddar project [BP Annex 15 P29 Table 8 Selected interventions] and that is to be delivered by 'business transformation programme' [Annex 15 P28]. This results is an allowance of £0.46m before we apply any efficiency challenge. “Cost estimates were usually based on high level scopes, which contained activity schedules, and sketches provided by ourselves, and were developed using the cost model we developed with Chandler KBS.”[Annex 15 Section 4.1.4 P19] | BP Table WS2, BRL.C5B.Technical Annex 15 Treatment Works Strategic Maintenance
Customer protection | Partial pass | Customers are protected by DWI letter of support and financial penalty | DWI letter of support
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 0.46
Apply Efficiency Challenge | 7.196%
Further analysis DWI Support letter for Cheddar WTW
The DWI Support letter for Cheddar WTW includes for covering of slow sand filters to reduce algal loading and prevent release of soluble metals, taste and odour issues, which will significantly improve system resilience. Capex for this identified in the letter is between £4.2 and £4.7m
The only scheme identified in the BP documents that is allocated to RW Deterioration is the trials extension at Cheddar £0.5m to which the BRL efficiency challenge of 7% is applied and this gives a value in the plan of £.46m. This is accepted because 1. it has gained DWI support and 2. improves confidence in final option selection.

## Deep dive_PRT
Deep dive sheet - Portsmouth Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | PRT
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 5.776
Ofwat view of allowance for AMP7 (£m) | 5.775
Assessment
Assessment gates |  |  | References
Need for investment | Pass | Portsmouth Water includes three schemes in this enhancement programme. The company has been served with a regulation 28 notice by DWI for Funtington, has a DWI letter of support for Maindell and the work at Lovedean has a DWI commend for support. | DWI letters and DWI regulation 28 notice.
Need for adjustment | N/A
Management control | Pass | Deterioration of raw waters is largely outside of management control. However PRT is also implementing catchment management schemes to mitigate effects.
Best option for customers | Partial pass | Funtington - PRT states “Based on analysis of water quality data …..Funtington's current raw water classification is C”, [Funtington Solutions Report dated July 18 p4]. The lowest Capex option to treat classification C raw water is Option 0a - capex £1.245m however PRT has selected the lowest cost option for classification D water - £2.2872m capex. This comrises UV treatment and an incresasew in contact for the 8ML/d works. The raw water is currently classed as C [solutions report July 18], but PRT were required to review risks presented by source water [DWI notice Oct 17] and to monitor for extended suite of microorganisms at the final sample point. We have found no evidence that the raw water is now classification D. We note that Atkins has produced a water quality report; however this was not found within the BP documents for the site. Maindell - The output of this works is 7 Ml/d. Options are costed and UV treatment the lowest NPV option selected. We note that an abandonment option is to be considered as part of Havant Thicket. Lovedean - The output from this works is 13.7Ml/d. PRT has discounted do nothing and selected blending at Nelson, this is the lowest net present value option from a list of costed options. | Funtington Solutions Report and DWI notice included within doc 9.11.14 WQ018
Robustness and efficiency of costs | Partial pass | Capital Programme costs have been audited by third party [Atkins] “The costs for these options have been calculated independently by consultants and appear to be reasonable.” [Summary Audit P8]. Atkins CBA summary report [doc 5160304-All-CAL-021 & Funtingdon Solution report] give Capex values of £2.463m for Funtingdon, £0.968m for Maindell; and £1.402m Lovedean. We note that the scheme level Capex values in BP Table commentary are higher; £2.872m, £1.186m & £1.717m. These uplifts are between 17% and 23%. PRT explain that the uplifts are for contingency and management [main dell crypto position paper] and these are reasonable levels of on-costs. Summary: PRT provides scheme level data and identifies the capacity of each WTW where work is required. Further evidence is required to demonstrate raw water classification at Funtingdon is class D. A CAC for Funtingdon which included UV treatment to treat class D water was passed in previous submission and is accepted again for IAP. | DG026_SAF Capital Programme_4.doc - Capital Programme Summary of Audit
Customer protection | Pass | Customers are protected by DWI notice and regulations
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 5.775
Apply Efficiency Challenge | 0%
Further analysis
PRT states: "Three Water Quality improvement schemes have triggered from the Company Drinking Water Safety Plans. These include the provision of additional treatment capability at Maindell (£1,186k) and Funtington (£2,872k) to address cryptosporidium concerns. The provision of blending capability at Lovedean of the Nelson with Lovedean water to alleviate increasing season nitrate levels at Lovedean (£1,717k)". [WS2 Table Commentary]. Summary information from the DWI correspondence is :
* DWI Letter of Support Maindell - Cryptosporidium - New borehole run to waste line. 2 UV reactors with all operational auxiliary equipment housed in a new permanent building. Glass trap and disposal facilities. Interconnecting pipework and valves. Site grounds upgrades. Site power upgrade of 20kW. Estimated capex £k1.170m.
* Lovedean WTW – Nitrate DWI Commend for Support
* Funtington WTW - DWI Reg 28 Notice disinfection failure dated October 17

## Deep dive_SEW
Deep dive sheet - South East Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | SEW
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 16.5086
Ofwat view of allowance for AMP7 (£m) | 16.3673
Assessment
Assessment gates |  |  | References
Need for investment | Pass | South East Water proposes two schemes to address raw water deterioration. DWI letters of support have been obtained for both. SEW identifies that it has completed groundwater modelling to predict future levels of nitrate in the Woodgarston catchment. Chromium level in treated water at College Avenue is the driver for investment at this site. The PCV levels at College Avenue are below the current PCV of 50 ug/l however is one of only three sites in the UK where levels exceed three ug/l [App 11 P43] and is above the new action level. Additionally advice from Public Health England is that exposure to chromium should be as low as reasonably practical [App 11, Annex B P51]. The company states “The Drinking Water Inspectorate has set a new action level for chromium VI concentrations in drinking water at 3μg/l. This level has regularly been exceeded at College Avenue water treatment works, despite taking measures to blend the water with other supplies”. [App11 Annex B P7]. | BP P117 App 11 P43 DWI letters of support.
Need for adjustment | N/A
Management control | Pass | Contamination of raw waters is largely outside of management control.
Best option for customers | Pass | SEW is also continuing to use catchment management, however this is not expected to deliver nitrate level reduction for 10 to 20 years [App 11 Annex B P51 & 53], an option is therefore required to address the short term need. SEW has considered a range of treatment and blending options and has selected the least cost option, this also provides supply resilience benefits. Cost benefit analysis is used to justify the scheme. [App11 Annex B P53-55]. For College Ave. SEW discounts abandonment for supply demand balance reasons. Currently water is blended but this still results in exceedance. [App11 Annex B P52]. SEW considers and discounts a number of treatment options to leave two options that it believes to be of similar cost. “The proposed solution is either coagulation and filtration or strong base ion exchange, according to the results of a pilot-scale study”.[App11 Annex B P7]. The company identifies the need for more detailed assessment to confirm option assessment. [App 9 P 56 P57] We consider this approach is appropriate. | App 11 Annex B P53 App 9
Robustness and efficiency of costs | Partial pass | SEW provides scheme level cost summaries for the options at Woodgarston and has selected the least cost option £3.12m [App 11 Annex B P54]. For the College Avenue scheme SEW has identified a Capex cost of £14.45m for Option 2 Ion exchange [App 11 , section 5.44 Table 16 & App9 P56] and £13.83m for reduction coagulation filtration [App 9 P56]. SEW states: “The proposed solution is either coagulation and filtration or strong base ion exchange, according to the results of a pilot-scale study”. [App 11, S 5.4.5 P44]. We recognise that the removal of chromium from raw water is an atypical process requirement and that trials are necessary to confirm the optimal treatment option. We make allowance for the lowest Capex option. We find no evidence of third party cost assurance. SEW states: “As a result we have applied an ambitious but realistic overall plan cost efficiency of 4.5 per cent .....Our industry-leading Unit Cost Database (UCDB) means we can quickly and accurately cost the investment in this plan, as it already contains actual costs for many types of schemes and projects already delivered.”[BP P114 115] We therefore apply a company cost challenge to determine the allowance. | BP P114 P115 App 11 App 11 Annex B. App 9 Water Quality
Customer protection | Pass | Schemes are DWI supported. Financial ODI penalty payments will also be applied in the event that DWI CRI target of 0 is not met.
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 16.5086
Apply Efficiency Challenge | 0.8562%
Further analysis
* College Avenue – Chromium - To install treatment facilities to reduce chromium concentrations in the treated water Estimated cost: Coagulation and filtration TOTEX: £15,250,847 Ion Exchange TOTEX: £13,420,713. DWI Support
* Woodgarston – Nitrate - Provision of nitrate removal treatment at Woodgarston to secure or facilitate compliance with the nitrate standard for drinking water quality reasons. - Estimated capital costs: £3.1m DWI Support
No evidence found [e.g. size of flows to be treated, detail in project descriptions ]. This information would inform our assessment.
.

## Deep dive_SSC
Deep dive sheet - South Staffs Water
The assessor and QA
Assessor's name | RP
Peer review (initials, date and QA log ref.) | AF 28/01/19
Company | SSC
Control | Wholesale water
Capex carried through deep dive AMP7 (£m) | 13.8241
Ofwat view of allowance for AMP7 (£m) | 6.4846
Assessment
Assessment gates |  |  | References
Need for investment | Partial pass | SSC proposes new treatment at three groundwater sites to address rising trends in nitrates and the presence of a pesticide called Chlorthal. [BP P137]. The sites identified for new treatment processes to address this RW deterioration are: Ashwood, Cookley - Kinver & Somerford Slade Heath. Schemes are justified on basis of either non-compliance or risk of compliance failures in the 2020 to 2025 period [App29 P63], however only one has DWI Letter of support with a second being given commend for support. For us to fully support the programme we would need further evidence of deteriorating ground water quality to support SSCs view that blending options are no longer viable. | DWI Letter of support/section 28 notice Kinver & Commend for support for Ashwood. BP P137 Appendix 29
Need for adjustment | N/A
Management control | N/A | Nitrates and pesticides in ground water are largely outside of management control.
Best option for customers | Partial pass | Other BP proposals include catchment management to reduce need for further treatment options [BP P151]. The selected option should deliver compliant drinking water to customers. SSC currently uses Ion exchange at other sites and proposes Ion exchange for these three sites. [App29 P64] We find evidence that the company considers alternative treatment options but we find no discussion of the relative costs and benefits of those options.. SSC discounts blending options but further discussion of the issues around blending would support its view. Ion exchange is an established method of treating already used by SSC. SSC select options 'following our thorough and detailed optimisation process in which we have considered both the benefits to service that the solutions will deliver and the cost of the investment........we also considered the installation of a Granular Activated Carbon (GAC) treatment solution for chlorthal, however, our analysis has indicated that ion exchange is a superior solution for reducing chlorthal concentrations..' [App29 P 64] Conclusion: To make a further allowance we require further evidence for discounting GAC and blending options. | BP P151 App29 P 64
Robustness and efficiency of costs | Partial pass | SSC identifies a hierarchy of methods to estimate scheme Capex. We assume costing of these schemes is top level - by experts based on a detailed scope of the scheme. [App29 P49] There is evidence of the scope of work priced being limited to ion exchange at 3 sites. Capex identified as Ashwood £3.85m, Cookley-Kinver £3.85m, Somerford - Slade Heath £4.7m [App29 P62] total £12.4m. SSC States:”£12.4million of this is for new treatment at three groundwater sites to address rising trends in nitrates and the presence of a pesticide called Chlorthal. Costain have independently priced this new treatment though we consider we will be able to deliver these schemes more efficiently through a competitive tendering process”.[BP P137] 'We consider that through competitive tendering, a strong procurement process and deriving economies from packaging these schemes, we can deliver these schemes significantly more efficiently. Therefore we have already applied an assumed efficiency to the Costain costing proposal. Costain’s original costings for the three sites were £13.7m and we have applied an efficiency reduction of £3.1m (23%) to these costs before including in our business plan.' [App29 P65] Summary: Work at 3 WTWs is identified however there is insufficient evidence provided to demonstrate DWI support for scheme at Slade Heath. Evidence to justify this scheme is required. Capex required for the schemes is unclear. £10.6 m after efficiency reduction [App29 P65] or £12.4m [BP] or £13.8m [Table WS2 entry]. We allow the £10.6m from SSCs App29 less the proportion that would be for Slade Heath £4.7m * (10.6/13.7). No information on the flows to be treated at the treatment plants is found. Identification of the scale and scope of the selected options permits a better assessment of cost. | App29 P49 BP P137 App29 P65
Customer protection | Pass | SSC proposes a financial ODI:water not safe to drink [BP App A3 P45]. Customers are protected from water quality and supply failures by other (common) performance commitments. | BP P119, BP App A3 P45
Affordability | N/A
Board assurance | N/A
Allowable costs [from submission] | 6.9635
Apply Efficiency Challenge | 6.878%
Further analysis
* Kinver-Cookley – Nitrate - Install and operate an Ion exchange treatment facility at Kinver-Cookley in order to reduce the risks of breaching the Nitrate standard within the connected supply zones. - Estimated capital costs: £3.5m [DWI letter] DWI Supported
* Ashwood WTW - provide Ion exchange treatment solutions for increasing resilience (by reducing nitrate & chlorthal) in water - Estimated value ? - DWI commend for support
* Somerford - Slade Heath - We find no evidence of DWI support.
SSC has identified customer WTP for safe water this is also a regulatory requirement. However we find insufficient data to demonstrate risk of failure to achieve drinking water standards at Slade Heath. We find conflicting cost information for the 3 schemes and limited evidence for discounting alternative treatment options.

## Analysis
Analysis and determination of allowance
£m 2017-18 prices
Investment to address raw water deterioration (THM, nitrates, Crypto, pesticides, others) - capex
|  | 2021 | 2022 | 2023 | 2024 | 2025 | AMP7 total | AMP7 total plus re-allocations | Totex - AMP7 total | Materiality | Shallow dive efficiency challenge | Shallow dive allowance | Deep dive allowance | Final allowance
| ANH | 5.1436 | 15.5414 | 2.0927 | 0 | 0 | 22.7777 | 22.7777 | 2814.0055 | 0.8094% | 15% | 0 | 15.4888 | 15.4888
| HDD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131.3026 | 0% | 0% | 0 |  | 0
| NES | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1729.884 | 0% | 0.0265% | 0 | 0 | 0
| NWT | 0.059093 | 0.059093 | 0.059093 | 0.059093 | 0.059093 | 0.29547 | 0.29547 | 2477.5035 | 0.01193% | 0% | 0.29547 |  | 0.29547
| SRN | 20.241 | 22.072 | 10.804 | 1.529 | 0.765 | 55.411 | 55.411 | 1226.604 | 4.517% | 10% | 0 | 49.8708 | 49.8708
| SVE | 4.016 | 7.836 | 10.855 | 7.024 | 4.318 | 34.049 | 34.049 | 3115.8042 | 1.093% | 0% | 0 | 21.8116 | 21.8116
| SWB | 6.319 | 9.943 | 18.523 | 17.398 | 11.44 | 63.623 | 77.232 | 894.252 | 7.115% | 0% | 0 | 41.5544 | 41.5544
| TMS | 9.0655 | 2.9582 | 0.44939 | 0 | 0 | 12.4731 | 12.4731 | 5658.2039 | 0.2204% | 13% | 10.8516 |  | 10.8516
| WSH | 0.483 | 0.505 | 0.137 | 0.137 | 0.137 | 1.399 | 10.399 | 1646.392 | 0.08497% | 0% | 10.399 |  | 10.399
| WSX | 1.2534 | 3.493 | 4.0933 | 1.4118 | 0.10558 | 10.3571 | 10.3571 | 660.3486 | 1.568% | 0% | 0 | 8 | 8
| YKY | 13.329 | 17.021 | 13.642 | 8.989 | 7.156 | 60.137 | 60.137 | 2024.423 | 2.971% | 10.35% | 0 | 35.9241 | 35.9241
| AFW | 0.972 | 2.2167 | 0.49778 | 0 | 0 | 3.6865 | 3.6865 | 1368.4611 | 0.2694% | 6.071% | 3.4627 |  | 3.4627
| BRL | 0.78 | 0.78 | 1.24 | 0.78 | 0.78 | 4.36 | 4.36 | 457.197 | 0.9536% | 7.196% | 0 | 0.4269 | 0.4269
| PRT | 2.872 | 1.186 | 0 | 1.46 | 0.258 | 5.776 | 5.776 | 223.944 | 2.579% | 0% | 0 | 5.775 | 5.775
| SES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.309 | 0% | 9.141% | 0 |  | 0
| SEW | 2.4285 | 2.3848 | 2.9194 | 4.8819 | 4.794 | 17.4086 | 17.4086 | 960.947 | 1.812% | 0.8562% | 0 | 16.3673 | 16.3673
| SSC | 0.29207 | 2.2165 | 2.2165 | 2.2165 | 6.8825 | 13.8241 | 13.8241 | 538.029 | 2.569% | 6.878% | 0 | 6.4846 | 6.4846
| Total | 67.2542 | 88.2127 | 67.5292 | 45.8863 | 36.6953 | 305.5776 | 335.7063 | 26180.6105 | 1.167% |  |  |  | 226.7123
Summary
* 14 Companies submitted * material * potential overlap with Taste Odour Colour
* alternates of blending and catchment management to addtional or upgraded treatment processes.
* time lag in catchment management - therefore other options likely to be needed for short medium term

## Allowance
Allowed costs
| Assessor's name | RP
Peer review (initials, date)
| BoN code | W3010CAW
| Enhancement line | Investment to address raw water deterioration (THM, nitrates, Crypto, pesticides, others)
| Control | Wholesale water
Cost allowance for AMP7 (£m)
| Company | Capex in business plan - wholesale water | Capex reallocated out to other lines | Capex reallocated in to this line | Net Capex reallocated in | Capex after reallocations | Modelled allowance | Capex allowed - wholesale water | Proportion of water resources | Capex allowed - water resources | Capex allowed - network plus
1 | ANH | 22.7777 | 0 | 0 | 0 | 22.7777 | 15.4888 | 15.4888 | 0% | 0 | 15.4888
2 | HDD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
3 | NES | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 0% | 0 | 0
4 | NWT | 0.29547 | 0 | 0 | 0 | 0.29547 | 0.29547 | 0.29547 | 100% | 0.29547 | 0
5 | SRN | 55.411 | 0 | 0 | 0 | 55.411 | 49.8708 | 49.8708 | 5.618% | 2.8018 | 47.069
6 | SVE | 34.049 | 0 | 0 | 0 | 34.049 | 21.8116 | 21.8116 | 0% | 0 | 21.8116
7 | SWB | 63.623 | 0 | 13.609 | 13.609 | 77.232 | 41.5544 | 41.5544 | 0% | 0 | 41.5544
8 | TMS | 12.4731 | 0 | 0 | 0 | 12.4731 | 10.8516 | 10.8516 | 32.42% | 3.5185 | 7.3332
9 | WSH | 1.399 | 0 | 9 | 9 | 10.399 | 10.399 | 10.399 | 0% | 0 | 10.399
10 | WSX | 10.3571 | 0 | 0 | 0 | 10.3571 | 8 | 8 | 5.097% | 0.40775 | 7.5923
11 | YKY | 60.137 | 0 | 0 | 0 | 60.137 | 35.9241 | 35.9241 | 0% | 0 | 35.9241
12 | AFW | 3.6865 | 0 | 0 | 0 | 3.6865 | 3.4627 | 3.4627 | 32.5% | 1.1252 | 2.3375
13 | BRL | 4.36 | 0 | 0 | 0 | 4.36 | 0.4269 | 0.4269 | 89.45% | 0.38186 | 0.04504
14 | PRT | 5.776 | 0 | 0 | 0 | 5.776 | 5.775 | 5.775 | 0% | 0 | 5.775
15 | SES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
16 | SEW | 17.4086 | 0 | 0 | 0 | 17.4086 | 16.3673 | 16.3673 | 2.238% | 0.36626 | 16.001
17 | SSC | 13.8241 | 0 | 0 | 0 | 13.8241 | 6.4846 | 6.4846 | 10.56% | 0.68502 | 5.7995
| Total | 305.5776 | 0 | 55.609 | 55.609 | 361.1866 | 226.7123 | 226.7123 |  | 9.5818 | 217.1306