## Cover
Cover sheet
Objective
To assess enhancement total expenditure (totex) submitted by companies in their PR19 business plan submissions for water resilience enhancement lines.
Approach
Due to the company-specific nature of this investment we undertake a deep dive of all companies’ plans. We allow investment on this line that relates to addressing low probability – high consequence risks, including those related to the National Flood Resilience Review. We reallocate investment where the resilience need is covered by other enhancement areas. In this way we ensure that our assessment is equitable across the industry.
In particular, for each proposed investment, to demonstrate the need for investment we seek evidence of:
1. The specific service failure mode and associated quantitative or semi-quantitative probability of failure the investment is proposing to address;
2. How mitigating against the failure is currently beyond management control;
3. The impact on customer service; and
4. How, should the failure occur, the consequence is currently beyond management control.
Principal changes since DD
We moved from a capex approach to a totex approach for slow track and significant scrutiny companies at draft determinations. For consistency, we are now including an opex allowance for fast track companies in order to have a totex allowance for all companies at final determinations.

## F_inputs
FM_E_WW_resilience
Acronym | Reference | Item description | Unit | Model | Description_input | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2020-25
ANH | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 23.6121 | 61.3919 | 94.3079 | 101.3288 | 49.3348
ANH | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 494.8537 | 569.1626 | 614.4832 | 601.174 | 466.5721
ANH | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0.1631 | 0.33587 | 0.6517 | 1.5109 | 3.6469
ANH | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
ANH | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
WSH | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 26.816 | 24.324 | 21.649 | 21.255 | 20.382
WSH | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 338.873 | 347.164 | 338.818 | 324.732 | 316.383
WSH | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
WSH | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
WSH | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
HDD | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 0.23 | 0.48 | 0.48 | 0.23 | 0.23
HDD | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 27.46 | 27.121 | 26.327 | 25.742 | 26.044
HDD | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
HDD | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0.5
HDD | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
NES | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 20.907 | 41.89 | 40.594 | 21.299 | 4.166
NES | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 348.078 | 368.717 | 360.499 | 337.229 | 311.733
NES | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
NES | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
NES | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
SVE | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 26.398 | 27.881 | 26.858 | 27.973 | 26.286
SVE | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 575.0657 | 631.1286 | 643.4347 | 635.4116 | 630.7635
SVE | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 2.347 | 2.414 | 2.418 | 2.394 | 2.462
SVE | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
SVE | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
SWB | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 2.881 | 5.581 | 11.398 | 11.671 | 11.639
SWB | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 164.926 | 179.669 | 192.194 | 181.702 | 175.761
SWB | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0.42 | 0.22 | 0.32 | 0.42 | 0.42
SWB | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
SWB | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 31.6
SRN | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
SRN | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 238.969 | 240.008 | 219.66 | 201.802 | 217.626
SRN | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
SRN | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
SRN | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
TMS | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 8.6514 | 20.2596 | 46.9096 | 58.9277 | 66.3151
TMS | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 1009.8378 | 1101.9036 | 1077.4233 | 1033.9695 | 997.9188
TMS | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0.2731 | 0.50551 | 1.173 | 1.8774
TMS | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
TMS | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
NWT | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 71.8074 | 13.4604 | 5.158 | 5.4351 | 12.0723
NWT | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 546.9142 | 511.026 | 491.8832 | 466.2618 | 461.4183
NWT | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
NWT | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
NWT | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 57.4
WSX | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 1.1613 | 1.1613 | 1.1613 | 1.1613 | 1.1613
WSX | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 134.2655 | 125.5988 | 144.2895 | 125.3448 | 120.5543
WSX | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
WSX | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
WSX | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
YKY | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
YKY | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 385.797 | 385.065 | 393.66 | 376.679 | 345.664
YKY | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
YKY | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
YKY | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
AFW | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 1.55 | 1.55 | 0 | 0 | 0
AFW | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 287.61 | 290.6915 | 281.3912 | 264.4597 | 241.8721
AFW | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
AFW | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
AFW | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
BRL | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 2.392 | 2.392 | 2.392 | 2.392 | 2.392
BRL | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 91.388 | 89.27 | 89.474 | 89.114 | 89.552
BRL | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
BRL | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
BRL | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
PRT | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 0 | 0 | 0.185 | 1.27 | 1.338
PRT | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 45.14 | 38.365 | 39.048 | 51.654 | 53.923
PRT | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
PRT | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
PRT | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
SEW | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 1.372 | 6.8895 | 11.7095 | 5.5899 | 8.3997
SEW | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 172.073 | 199.614 | 208.204 | 186.195 | 194.588
SEW | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
SEW | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
SEW | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
SSC | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 1.2975 | 0.64114 | 1.1367 | 0.23712 | 0.7887
SSC | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 113.2581 | 115.4825 | 116.3865 | 93.9133 | 96.8046
SSC | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
SSC | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
SSC | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0
SES | C_W3011CAW_PR19CA001 | Total wholesale water - Resilience | £m | Price Review 2019 |  | 1.643 | 4.647 | 1.46 | 0.558 | 0.558
SES | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 52.777 | 57.544 | 52.131 | 46.371 | 45.346
SES | WS2022CAW | Enhancement expenditure by purpose ~ operating - Resilience - Total | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0
SES | C_W3011CAC_PR19WR | Total CAC-WW_Resilience-WR | £m | Price Review 2019 | [6 empty] | 0
SES | C_W3011CAC_PR19WN | Total CAC-WW_Resilience-WN | £m | Price Review 2019 | [6 empty] | 0

## Data
Data
£m 2017-18 prices
|  |  | C_W3011CAW_PR19CA001 | C_W3026TECAW_PR19CA001 | WS2022CAW
Code | Company | Financial Year | £m Total wholesale water - Resilience | £m 2017-18 prices, Totex wholesale water (including cash items and atypical expenditure) | £m Enhancement expenditure by purpose ~ operating - Resilience - Total
ANH21 | ANH | 2020-21 | 23.6121 | 494.8537 | 0.1631
ANH22 | ANH | 2021-22 | 61.3919 | 569.1626 | 0.33587
ANH23 | ANH | 2022-23 | 94.3079 | 614.4832 | 0.6517
ANH24 | ANH | 2023-24 | 101.3288 | 601.174 | 1.5109
ANH25 | ANH | 2024-25 | 49.3348 | 466.5721 | 3.6469
NES21 | NES | 2020-21 | 20.907 | 348.078 | 0
NES22 | NES | 2021-22 | 41.89 | 368.717 | 0
NES23 | NES | 2022-23 | 40.594 | 360.499 | 0
NES24 | NES | 2023-24 | 21.299 | 337.229 | 0
NES25 | NES | 2024-25 | 4.166 | 311.733 | 0
NWT21 | NWT | 2020-21 | 71.8074 | 546.9142 | 0
NWT22 | NWT | 2021-22 | 13.4604 | 511.026 | 0
NWT23 | NWT | 2022-23 | 5.158 | 491.8832 | 0
NWT24 | NWT | 2023-24 | 5.4351 | 466.2618 | 0
NWT25 | NWT | 2024-25 | 12.0723 | 461.4183 | 0
SRN21 | SRN | 2020-21 | 0 | 238.969 | 0
SRN22 | SRN | 2021-22 | 0 | 240.008 | 0
SRN23 | SRN | 2022-23 | 0 | 219.66 | 0
SRN24 | SRN | 2023-24 | 0 | 201.802 | 0
SRN25 | SRN | 2024-25 | 0 | 217.626 | 0
SVT21 | SVT | 2020-21 | #N/A | #N/A | #N/A
SVT22 | SVT | 2021-22 | #N/A | #N/A | #N/A
SVT23 | SVT | 2022-23 | #N/A | #N/A | #N/A
SVT24 | SVT | 2023-24 | #N/A | #N/A | #N/A
SVT25 | SVT | 2024-25 | #N/A | #N/A | #N/A
SWT21 | SWT | 2020-21 | #N/A | #N/A | #N/A
SWT22 | SWT | 2021-22 | #N/A | #N/A | #N/A
SWT23 | SWT | 2022-23 | #N/A | #N/A | #N/A
SWT24 | SWT | 2023-24 | #N/A | #N/A | #N/A
SWT25 | SWT | 2024-25 | #N/A | #N/A | #N/A
SWB21 | SWB | 2020-21 | 2.881 | 164.926 | 0.42
SWB22 | SWB | 2021-22 | 5.581 | 179.669 | 0.22
SWB23 | SWB | 2022-23 | 11.398 | 192.194 | 0.32
SWB24 | SWB | 2023-24 | 11.671 | 181.702 | 0.42
SWB25 | SWB | 2024-25 | 11.639 | 175.761 | 0.42
TMS21 | TMS | 2020-21 | 8.6514 | 1009.8378 | 0
TMS22 | TMS | 2021-22 | 20.2596 | 1101.9036 | 0.2731
TMS23 | TMS | 2022-23 | 46.9096 | 1077.4233 | 0.50551
TMS24 | TMS | 2023-24 | 58.9277 | 1033.9695 | 1.173
TMS25 | TMS | 2024-25 | 66.3151 | 997.9188 | 1.8774
WSH21 | WSH | 2020-21 | 26.816 | 338.873 | 0
WSH22 | WSH | 2021-22 | 24.324 | 347.164 | 0
WSH23 | WSH | 2022-23 | 21.649 | 338.818 | 0
WSH24 | WSH | 2023-24 | 21.255 | 324.732 | 0
WSH25 | WSH | 2024-25 | 20.382 | 316.383 | 0
WSX21 | WSX | 2020-21 | 1.1613 | 134.2655 | 0
WSX22 | WSX | 2021-22 | 1.1613 | 125.5988 | 0
WSX23 | WSX | 2022-23 | 1.1613 | 144.2895 | 0
WSX24 | WSX | 2023-24 | 1.1613 | 125.3448 | 0
WSX25 | WSX | 2024-25 | 1.1613 | 120.5543 | 0
YKY21 | YKY | 2020-21 | 0 | 385.797 | 0
YKY22 | YKY | 2021-22 | 0 | 385.065 | 0
YKY23 | YKY | 2022-23 | 0 | 393.66 | 0
YKY24 | YKY | 2023-24 | 0 | 376.679 | 0
YKY25 | YKY | 2024-25 | 0 | 345.664 | 0
AFW21 | AFW | 2020-21 | 1.55 | 287.61 | 0
AFW22 | AFW | 2021-22 | 1.55 | 290.6915 | 0
AFW23 | AFW | 2022-23 | 0 | 281.3912 | 0
AFW24 | AFW | 2023-24 | 0 | 264.4597 | 0
AFW25 | AFW | 2024-25 | 0 | 241.8721 | 0
BRL21 | BRL | 2020-21 | 2.392 | 91.388 | 0
BRL22 | BRL | 2021-22 | 2.392 | 89.27 | 0
BRL23 | BRL | 2022-23 | 2.392 | 89.474 | 0
BRL24 | BRL | 2023-24 | 2.392 | 89.114 | 0
BRL25 | BRL | 2024-25 | 2.392 | 89.552 | 0
BWH21 | BWH | 2020-21 | #N/A | #N/A | #N/A
BWH22 | BWH | 2021-22 | #N/A | #N/A | #N/A
BWH23 | BWH | 2022-23 | #N/A | #N/A | #N/A
BWH24 | BWH | 2023-24 | #N/A | #N/A | #N/A
BWH25 | BWH | 2024-25 | #N/A | #N/A | #N/A
DVW21 | DVW | 2020-21 | #N/A | #N/A | #N/A
DVW22 | DVW | 2021-22 | #N/A | #N/A | #N/A
DVW23 | DVW | 2022-23 | #N/A | #N/A | #N/A
DVW24 | DVW | 2023-24 | #N/A | #N/A | #N/A
DVW25 | DVW | 2024-25 | #N/A | #N/A | #N/A
PRT21 | PRT | 2020-21 | 0 | 45.14 | 0
PRT22 | PRT | 2021-22 | 0 | 38.365 | 0
PRT23 | PRT | 2022-23 | 0.185 | 39.048 | 0
PRT24 | PRT | 2023-24 | 1.27 | 51.654 | 0
PRT25 | PRT | 2024-25 | 1.338 | 53.923 | 0
SES21 | SES | 2020-21 | 1.643 | 52.777 | 0
SES22 | SES | 2021-22 | 4.647 | 57.544 | 0
SES23 | SES | 2022-23 | 1.46 | 52.131 | 0
SES24 | SES | 2023-24 | 0.558 | 46.371 | 0
SES25 | SES | 2024-25 | 0.558 | 45.346 | 0
SEW21 | SEW | 2020-21 | 1.372 | 172.073 | 0
SEW22 | SEW | 2021-22 | 6.8895 | 199.614 | 0
SEW23 | SEW | 2022-23 | 11.7095 | 208.204 | 0
SEW24 | SEW | 2023-24 | 5.5899 | 186.195 | 0
SEW25 | SEW | 2024-25 | 8.3997 | 194.588 | 0
SSC21 | SSC | 2020-21 | 1.2975 | 113.2581 | 0
SSC22 | SSC | 2021-22 | 0.64114 | 115.4825 | 0
SSC23 | SSC | 2022-23 | 1.1367 | 116.3865 | 0
SSC24 | SSC | 2023-24 | 0.23712 | 93.9133 | 0
SSC25 | SSC | 2024-25 | 0.7887 | 96.8046 | 0
SVE21 | SVE | 2020-21 | 26.398 | 575.0657 | 2.347
SVE22 | SVE | 2021-22 | 27.881 | 631.1286 | 2.414
SVE23 | SVE | 2022-23 | 26.858 | 643.4347 | 2.418
SVE24 | SVE | 2023-24 | 27.973 | 635.4116 | 2.394
SVE25 | SVE | 2024-25 | 26.286 | 630.7635 | 2.462
HDD21 | HDD | 2020-21 | 0.23 | 27.46 | 0
HDD22 | HDD | 2021-22 | 0.48 | 27.121 | 0
HDD23 | HDD | 2022-23 | 0.48 | 26.327 | 0
HDD24 | HDD | 2023-24 | 0.23 | 25.742 | 0
HDD25 | HDD | 2024-25 | 0.23 | 26.044 | 0

## Data_Override
Data
£m 2017-18 prices
|  |  | C_W3011CAW_PR19CA001 | C_W3026TECAW_PR19CA001 | WS2022CAW
Code | Company | Financial Year | £m Total wholesale water - Resilience | £m 2017-18 prices, Totex wholesale water (including cash items and atypical expenditure) | £m Enhancement expenditure by purpose ~ operating - Resilience - Total | Comments on overrides made
ANH21 | ANH | 2020-21
ANH22 | ANH | 2021-22
ANH23 | ANH | 2022-23
ANH24 | ANH | 2023-24
ANH25 | ANH | 2024-25
NES21 | NES | 2020-21
NES22 | NES | 2021-22
NES23 | NES | 2022-23
NES24 | NES | 2023-24
NES25 | NES | 2024-25
NWT21 | NWT | 2020-21
NWT22 | NWT | 2021-22
NWT23 | NWT | 2022-23
NWT24 | NWT | 2023-24
NWT25 | NWT | 2024-25
SRN21 | SRN | 2020-21
SRN22 | SRN | 2021-22
SRN23 | SRN | 2022-23
SRN24 | SRN | 2023-24
SRN25 | SRN | 2024-25
SVT21 | SVT | 2020-21
SVT22 | SVT | 2021-22
SVT23 | SVT | 2022-23
SVT24 | SVT | 2023-24
SVT25 | SVT | 2024-25
SWT21 | SWT | 2020-21
SWT22 | SWT | 2021-22
SWT23 | SWT | 2022-23
SWT24 | SWT | 2023-24
SWT25 | SWT | 2024-25
SWB21 | SWB | 2020-21
SWB22 | SWB | 2021-22
SWB23 | SWB | 2022-23
SWB24 | SWB | 2023-24
SWB25 | SWB | 2024-25
TMS21 | TMS | 2020-21
TMS22 | TMS | 2021-22
TMS23 | TMS | 2022-23
TMS24 | TMS | 2023-24
TMS25 | TMS | 2024-25
WSH21 | WSH | 2020-21
WSH22 | WSH | 2021-22
WSH23 | WSH | 2022-23
WSH24 | WSH | 2023-24
WSH25 | WSH | 2024-25
WSX21 | WSX | 2020-21
WSX22 | WSX | 2021-22
WSX23 | WSX | 2022-23
WSX24 | WSX | 2023-24
WSX25 | WSX | 2024-25
YKY21 | YKY | 2020-21
YKY22 | YKY | 2021-22
YKY23 | YKY | 2022-23
YKY24 | YKY | 2023-24
YKY25 | YKY | 2024-25
AFW21 | AFW | 2020-21
AFW22 | AFW | 2021-22
AFW23 | AFW | 2022-23
AFW24 | AFW | 2023-24
AFW25 | AFW | 2024-25
BRL21 | BRL | 2020-21
BRL22 | BRL | 2021-22
BRL23 | BRL | 2022-23
BRL24 | BRL | 2023-24
BRL25 | BRL | 2024-25
BWH21 | BWH | 2020-21
BWH22 | BWH | 2021-22
BWH23 | BWH | 2022-23
BWH24 | BWH | 2023-24
BWH25 | BWH | 2024-25
DVW21 | DVW | 2020-21
DVW22 | DVW | 2021-22
DVW23 | DVW | 2022-23
DVW24 | DVW | 2023-24
DVW25 | DVW | 2024-25
PRT21 | PRT | 2020-21
PRT22 | PRT | 2021-22
PRT23 | PRT | 2022-23
PRT24 | PRT | 2023-24
PRT25 | PRT | 2024-25
SES21 | SES | 2020-21
SES22 | SES | 2021-22
SES23 | SES | 2022-23
SES24 | SES | 2023-24
SES25 | SES | 2024-25
SEW21 | SEW | 2020-21
SEW22 | SEW | 2021-22
SEW23 | SEW | 2022-23
SEW24 | SEW | 2023-24
SEW25 | SEW | 2024-25
SSC21 | SSC | 2020-21
SSC22 | SSC | 2021-22
SSC23 | SSC | 2022-23
SSC24 | SSC | 2023-24
SSC25 | SSC | 2024-25
SVE21 | SVE | 2020-21 |  |  | 0.261 | AF: Taken 2.086 from value to rebase AMP7 opex to 1 April 2020 (2.086 = 2.160 in 2017-18 prices)
SVE22 | SVE | 2021-22 |  |  | 0.328 | AF: Taken 2.086 from value to rebase AMP7 opex to 1 April 2020 (2.086 = 2.160 in 2017-18 prices)
SVE23 | SVE | 2022-23 |  |  | 0.332 | AF: Taken 2.086 from value to rebase AMP7 opex to 1 April 2020 (2.086 = 2.160 in 2017-18 prices)
SVE24 | SVE | 2023-24 |  |  | 0.308 | AF: Taken 2.086 from value to rebase AMP7 opex to 1 April 2020 (2.086 = 2.160 in 2017-18 prices)
SVE25 | SVE | 2024-25 |  |  | 0.376 | AF: Taken 2.086 from value to rebase AMP7 opex to 1 April 2020 (2.086 = 2.160 in 2017-18 prices)
HDD21 | HDD | 2020-21
HDD22 | HDD | 2021-22
HDD23 | HDD | 2022-23
HDD24 | HDD | 2023-24
HDD25 | HDD | 2024-25

## Data_Final
Data
£m 2017-18 prices
|  |  | C_W3011CAW_PR19CA001 | C_W3026TECAW_PR19CA001 | WS2022CAW
Code | Company | Financial Year | £m Total wholesale water - Resilience | £m 2017-18 prices, Totex wholesale water (including cash items and atypical expenditure) | £m Enhancement expenditure by purpose ~ operating - Resilience - Total
ANH21 | ANH | 2020-21 | 23.6121 | 494.8537 | 0.1631
ANH22 | ANH | 2021-22 | 61.3919 | 569.1626 | 0.33587
ANH23 | ANH | 2022-23 | 94.3079 | 614.4832 | 0.6517
ANH24 | ANH | 2023-24 | 101.3288 | 601.174 | 1.5109
ANH25 | ANH | 2024-25 | 49.3348 | 466.5721 | 3.6469
NES21 | NES | 2020-21 | 20.907 | 348.078 | 0
NES22 | NES | 2021-22 | 41.89 | 368.717 | 0
NES23 | NES | 2022-23 | 40.594 | 360.499 | 0
NES24 | NES | 2023-24 | 21.299 | 337.229 | 0
NES25 | NES | 2024-25 | 4.166 | 311.733 | 0
NWT21 | NWT | 2020-21 | 71.8074 | 546.9142 | 0
NWT22 | NWT | 2021-22 | 13.4604 | 511.026 | 0
NWT23 | NWT | 2022-23 | 5.158 | 491.8832 | 0
NWT24 | NWT | 2023-24 | 5.4351 | 466.2618 | 0
NWT25 | NWT | 2024-25 | 12.0723 | 461.4183 | 0
SRN21 | SRN | 2020-21 | 0 | 238.969 | 0
SRN22 | SRN | 2021-22 | 0 | 240.008 | 0
SRN23 | SRN | 2022-23 | 0 | 219.66 | 0
SRN24 | SRN | 2023-24 | 0 | 201.802 | 0
SRN25 | SRN | 2024-25 | 0 | 217.626 | 0
SVT21 | SVT | 2020-21 | #N/A | #N/A | #N/A
SVT22 | SVT | 2021-22 | #N/A | #N/A | #N/A
SVT23 | SVT | 2022-23 | #N/A | #N/A | #N/A
SVT24 | SVT | 2023-24 | #N/A | #N/A | #N/A
SVT25 | SVT | 2024-25 | #N/A | #N/A | #N/A
SWT21 | SWT | 2020-21 | #N/A | #N/A | #N/A
SWT22 | SWT | 2021-22 | #N/A | #N/A | #N/A
SWT23 | SWT | 2022-23 | #N/A | #N/A | #N/A
SWT24 | SWT | 2023-24 | #N/A | #N/A | #N/A
SWT25 | SWT | 2024-25 | #N/A | #N/A | #N/A
SWB21 | SWB | 2020-21 | 2.881 | 164.926 | 0.42
SWB22 | SWB | 2021-22 | 5.581 | 179.669 | 0.22
SWB23 | SWB | 2022-23 | 11.398 | 192.194 | 0.32
SWB24 | SWB | 2023-24 | 11.671 | 181.702 | 0.42
SWB25 | SWB | 2024-25 | 11.639 | 175.761 | 0.42
TMS21 | TMS | 2020-21 | 8.6514 | 1009.8378 | 0
TMS22 | TMS | 2021-22 | 20.2596 | 1101.9036 | 0.2731
TMS23 | TMS | 2022-23 | 46.9096 | 1077.4233 | 0.50551
TMS24 | TMS | 2023-24 | 58.9277 | 1033.9695 | 1.173
TMS25 | TMS | 2024-25 | 66.3151 | 997.9188 | 1.8774
WSH21 | WSH | 2020-21 | 26.816 | 338.873 | 0
WSH22 | WSH | 2021-22 | 24.324 | 347.164 | 0
WSH23 | WSH | 2022-23 | 21.649 | 338.818 | 0
WSH24 | WSH | 2023-24 | 21.255 | 324.732 | 0
WSH25 | WSH | 2024-25 | 20.382 | 316.383 | 0
WSX21 | WSX | 2020-21 | 1.1613 | 134.2655 | 0
WSX22 | WSX | 2021-22 | 1.1613 | 125.5988 | 0
WSX23 | WSX | 2022-23 | 1.1613 | 144.2895 | 0
WSX24 | WSX | 2023-24 | 1.1613 | 125.3448 | 0
WSX25 | WSX | 2024-25 | 1.1613 | 120.5543 | 0
YKY21 | YKY | 2020-21 | 0 | 385.797 | 0
YKY22 | YKY | 2021-22 | 0 | 385.065 | 0
YKY23 | YKY | 2022-23 | 0 | 393.66 | 0
YKY24 | YKY | 2023-24 | 0 | 376.679 | 0
YKY25 | YKY | 2024-25 | 0 | 345.664 | 0
AFW21 | AFW | 2020-21 | 1.55 | 287.61 | 0
AFW22 | AFW | 2021-22 | 1.55 | 290.6915 | 0
AFW23 | AFW | 2022-23 | 0 | 281.3912 | 0
AFW24 | AFW | 2023-24 | 0 | 264.4597 | 0
AFW25 | AFW | 2024-25 | 0 | 241.8721 | 0
BRL21 | BRL | 2020-21 | 2.392 | 91.388 | 0
BRL22 | BRL | 2021-22 | 2.392 | 89.27 | 0
BRL23 | BRL | 2022-23 | 2.392 | 89.474 | 0
BRL24 | BRL | 2023-24 | 2.392 | 89.114 | 0
BRL25 | BRL | 2024-25 | 2.392 | 89.552 | 0
BWH21 | BWH | 2020-21 | #N/A | #N/A | #N/A
BWH22 | BWH | 2021-22 | #N/A | #N/A | #N/A
BWH23 | BWH | 2022-23 | #N/A | #N/A | #N/A
BWH24 | BWH | 2023-24 | #N/A | #N/A | #N/A
BWH25 | BWH | 2024-25 | #N/A | #N/A | #N/A
DVW21 | DVW | 2020-21 | #N/A | #N/A | #N/A
DVW22 | DVW | 2021-22 | #N/A | #N/A | #N/A
DVW23 | DVW | 2022-23 | #N/A | #N/A | #N/A
DVW24 | DVW | 2023-24 | #N/A | #N/A | #N/A
DVW25 | DVW | 2024-25 | #N/A | #N/A | #N/A
PRT21 | PRT | 2020-21 | 0 | 45.14 | 0
PRT22 | PRT | 2021-22 | 0 | 38.365 | 0
PRT23 | PRT | 2022-23 | 0.185 | 39.048 | 0
PRT24 | PRT | 2023-24 | 1.27 | 51.654 | 0
PRT25 | PRT | 2024-25 | 1.338 | 53.923 | 0
SES21 | SES | 2020-21 | 1.643 | 52.777 | 0
SES22 | SES | 2021-22 | 4.647 | 57.544 | 0
SES23 | SES | 2022-23 | 1.46 | 52.131 | 0
SES24 | SES | 2023-24 | 0.558 | 46.371 | 0
SES25 | SES | 2024-25 | 0.558 | 45.346 | 0
SEW21 | SEW | 2020-21 | 1.372 | 172.073 | 0
SEW22 | SEW | 2021-22 | 6.8895 | 199.614 | 0
SEW23 | SEW | 2022-23 | 11.7095 | 208.204 | 0
SEW24 | SEW | 2023-24 | 5.5899 | 186.195 | 0
SEW25 | SEW | 2024-25 | 8.3997 | 194.588 | 0
SSC21 | SSC | 2020-21 | 1.2975 | 113.2581 | 0
SSC22 | SSC | 2021-22 | 0.64114 | 115.4825 | 0
SSC23 | SSC | 2022-23 | 1.1367 | 116.3865 | 0
SSC24 | SSC | 2023-24 | 0.23712 | 93.9133 | 0
SSC25 | SSC | 2024-25 | 0.7887 | 96.8046 | 0
SVE21 | SVE | 2020-21 | 26.398 | 575.0657 | 0.261
SVE22 | SVE | 2021-22 | 27.881 | 631.1286 | 0.328
SVE23 | SVE | 2022-23 | 26.858 | 643.4347 | 0.332
SVE24 | SVE | 2023-24 | 27.973 | 635.4116 | 0.308
SVE25 | SVE | 2024-25 | 26.286 | 630.7635 | 0.376
HDD21 | HDD | 2020-21 | 0.23 | 27.46 | 0
HDD22 | HDD | 2021-22 | 0.48 | 27.121 | 0
HDD23 | HDD | 2022-23 | 0.48 | 26.327 | 0
HDD24 | HDD | 2023-24 | 0.23 | 25.742 | 0
HDD25 | HDD | 2024-25 | 0.23 | 26.044 | 0

## Analysis
Analysis and determination of allowance
£m 2017-18 prices
TOTEX
£m Total wholesale water - Resilience
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | AMP7 total | Net reallocations of totex | Totex after reallocations for assessment | Totex carried through to assessment | Comments on overrides | Totex - AMP7 total | Materiality | Assessment method | Deep dive efficiency challenge | Deep dive allowance
| ANH | 23.7752 | 61.7278 | 94.9596 | 102.8398 | 52.9817 | 336.2841 | -280.6382 | 55.6459 | 55.6459 | n/a | 2746.2456 | 2.026% | Deep dive | 0.1 | see deep dive sheet
| HDD | 0.23 | 0.48 | 0.48 | 0.23 | 0.23 | 1.65 | 0 | 1.65 | 1.65 | n/a | 132.694 | 1.243% | Deep dive | 0.05 | see deep dive sheet
| NES | 20.907 | 41.89 | 40.594 | 21.299 | 4.166 | 128.856 | -1.46 | 127.396 | 127.396 | n/a | 1726.256 | 7.38% | Deep dive | 0.05 | see deep dive sheet
| NWT | 71.8074 | 13.4604 | 5.158 | 5.4351 | 12.0723 | 107.9332 | 0 | 107.9332 | 107.9332 | n/a | 2477.5035 | 4.357% | Deep dive | 0.05 | see deep dive sheet
| SRN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 1118.065 | 0% | Shallow dive | 0.083305 | 0
| SVE | 26.659 | 28.209 | 27.19 | 28.281 | 26.662 | 137.001 | 0 | 137.001 | 137.001 | n/a | 3115.8042 | 4.397% | Deep dive | 0.05 | see deep dive sheet
| SWB | 3.301 | 5.801 | 11.718 | 12.091 | 12.059 | 44.97 | 9.493 | 54.463 | 54.463 | n/a | 894.252 | 6.09% | Deep dive | 0.05 | see deep dive sheet
| TMS | 8.6514 | 20.5327 | 47.4151 | 60.1007 | 68.1924 | 204.8924 | 0 | 204.8924 | 204.8924 | n/a | 5221.0529 | 3.924% | Deep dive | 0.062282 | see deep dive sheet
| WSH | 26.816 | 24.324 | 21.649 | 21.255 | 20.382 | 114.426 | -0.54 | 113.886 | 113.886 | n/a | 1665.97 | 6.836% | Deep dive | 0.05 | see deep dive sheet
| WSX | 1.1613 | 1.1613 | 1.1613 | 1.1613 | 1.1613 | 5.8067 | 0 | 5.8067 | 5.8067 | n/a | 650.053 | 0.8933% | Deep dive | 0.05 | see deep dive sheet
| YKY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 1886.865 | 0% | Shallow dive | 0 | 0
| AFW | 1.55 | 1.55 | 0 | 0 | 0 | 3.1 | 12.366 | 15.466 | 15.466 | n/a | 1366.0245 | 1.132% | Deep dive | 0.05 | see deep dive sheet
| BRL | 2.392 | 2.392 | 2.392 | 2.392 | 2.392 | 11.96 | 0 | 11.96 | 11.96 | n/a | 448.798 | 2.665% | Deep dive | 0.1 | see deep dive sheet
| PRT | 0 | 0 | 0.185 | 1.27 | 1.338 | 2.793 | 0 | 2.793 | 2.793 | n/a | 228.13 | 1.224% | Deep dive | 0.05 | see deep dive sheet
| SES | 1.643 | 4.647 | 1.46 | 0.558 | 0.558 | 8.866 | 0 | 8.866 | 8.866 | n/a | 254.169 | 3.488% | Deep dive | 0.05 | see deep dive sheet
| SEW | 1.372 | 6.8895 | 11.7095 | 5.5899 | 8.3997 | 33.9605 | 0 | 33.9605 | 33.9605 | n/a | 960.674 | 3.535% | Deep dive | 0.1 | see deep dive sheet
| SSC | 1.2975 | 0.64114 | 1.1367 | 0.23712 | 0.7887 | 4.1012 | 0 | 4.1012 | 4.1012 | n/a | 535.8451 | 0.7654% | Deep dive | 0.05 | see deep dive sheet
| Total | 191.5629 | 213.7059 | 267.2082 | 262.7399 | 211.3832 | 1146.6001 | -260.7792 | 885.8209 | 885.8209 |  | 25428.4018 | 4.509%

## Allowance
FD - Allowed costs | [9 empty] | DD - Allowed costs | [9 empty] | IAP - Allowed costs
| Assessor's initials | AC, NR, GG | [8 empty] | Assessor's initials | AC, NR, GG | [8 empty] | Assessor's name | PD, JN, MG,
| Peer review (initials, date) | AF 12/12/19 | [8 empty] | Peer review (initials, date) | GG, NR, AC | [8 empty] | Peer review (initials, date)
| BoN code | W3011CAW + WS2022CAW | [8 empty] | BoN code | W3011CAW + WS2022CAW | [8 empty] | BoN code | W3011CAW
| Enhancement line | Resilience | [8 empty] | Enhancement line | Resilience | [8 empty] | Enhancement line | £m, Enhancement capex water - Resilience
[21 empty] | Control | Wholesale water
Cost allowance for 2020-25 (£m of 2017-18) | [9 empty] | Cost allowance for 2020-25 (£m of 2017-18)
Cost allowance for AMP7 (£m)
| Company | Totex in business plan - wholesale water | Net totex reallocated in | Totex after reallocations | Modelled allowance | Totex allowed - wholesale water | Totex allowed - water resources | Totex allowed - network plus | Proportion of water resources |  | Company | Totex in business plan - wholesale water | Net totex reallocated in | Totex after reallocations | Modelled allowance | Totex allowed - wholesale water | Totex allowed - water resources | Totex allowed - network plus | Proportion of water resources |  | Company | Capex in business plan - wholesale water | Capex reallocated out to other lines | Capex reallocated in to this line | Net Capex reallocated in | Capex after reallocations | Modelled allowance | Capex allowed - wholesale water | Proportion of water resources | Capex allowed - water resources | Capex allowed - network plus
1 | ANH | 336.2841 | -280.6382 | 55.6459 | 19.0482 | 19.0482 | 0 | 19.0482 | 0% | 1 | ANH | 336.2841 | -280.6382 | 55.6459 | 17.082 | 17.082 | 0.14299 | 16.939 | 0.8371% | 1 | ANH | 358.0496 | 335.265 | 0.038711 | -335.2263 | 22.8233 | 15.5199 | 15.5199 | 0.661% | 0.10259 | 15.4173
2 | HDD | 1.65 | 0 | 1.65 | 0.5 | 0.5 | 0 | 0.5 | 0% | 2 | HDD | 1.65 | 0 | 1.65 | 0.5 | 0.5 | 0 | 0.5 | 0% | 2 | HDD | 1.65 | 0 | 0 | 0 | 1.65 | 1.65 | 1.65 | 0% | 0 | 1.65
3 | NES | 128.856 | -1.46 | 127.396 | 63.7089 | 63.7089 | 0 | 63.7089 | 0% | 3 | NES | 128.856 | -1.46 | 127.396 | 55.7745 | 55.7745 | 0 | 55.7745 | 0% | 3 | NES | 153.187 | 53.2 | 0 | -53.2 | 99.987 | 50.9865 | 50.9865 | 0% | 0 | 50.9865
4 | NWT | 107.9332 | 0 | 107.9332 | 78.5852 | 78.5852 | 0 | 78.5852 | 0% | 4 | NWT | 107.9332 | 0 | 107.9332 | 78.5396 | 78.5396 | 0 | 78.5396 | 0% | 4 | NWT | 107.9332 | 13 | 0 | -13 | 22.2522 | 22.2522 | 22.2522 | 0% | 0 | 22.2522
5 | SRN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 5 | SRN | 0 | 0 | 0 | - | 0 | 0 | 0 | 0% | 5 | SRN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
6 | SVE | 137.001 | 0 | 137.001 | 107.15 | 107.15 | 1.3929 | 105.7571 | 1.3% | 6 | SVE | 137.001 | 0 | 137.001 | 107.15 | 107.15 | 1.0902 | 106.0598 | 1.017% | 6 | SVE | 135.396 | 0 | 0 | 0 | 135.396 | 107.15 | 107.15 | 1.108% | 1.1871 | 105.9629
7 | SWB | 44.97 | 9.493 | 54.463 | 38.7726 | 38.7726 | 0 | 38.7726 | 0% | 7 | SWB | 44.97 | 9.493 | 54.463 | 33.4446 | 33.4446 | 0 | 33.4446 | 0% | 7 | SWB | 43.17 | 12.89 | 11.975 | -0.915 | 8.991 | 7.1928 | 7.1928 | 0% | 0 | 7.1928
8 | TMS | 204.8924 | 0 | 204.8924 | 197.3541 | 197.3541 | 0 | 197.3541 | 0% | 8 | TMS | 204.8924 | 0 | 204.8924 | 73.6888 | 73.6888 | 0 | 73.6888 | 0% | 8 | TMS | 208.7774 | 0 | 0 | 0 | 208.7774 | 109.8858 | 109.8858 | 0% | 0 | 109.8858
9 | WSH | 114.426 | -0.54 | 113.886 | 18.7401 | 18.7401 | 0 | 18.7401 | 0% | 9 | WSH | 114.426 | -0.54 | 113.886 | 3.61 | 3.61 | 0.0050163 | 3.605 | 0.139% | 9 | WSH | 124.347 | 85.92 | 0 | -85.92 | 38.427 | 5.31 | 5.31 | 24.4% | 1.2957 | 4.0143
10 | WSX | 5.8067 | 0 | 5.8067 | 0.916 | 0.916 | 0 | 0.916 | 0% | 10 | WSX | 5.8067 | 0 | 5.8067 | 0.69616 | 0.69616 | 0.063287 | 0.63287 | 9.091% | 10 | WSX | 8.5517 | 3.25 | 0 | -3.25 | 5.3017 | 5.3017 | 5.3017 | 0% | 0 | 5.3017
11 | YKY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 11 | YKY | 0 | 0 | 0 | - | 0 | 0 | 0 | 0% | 11 | YKY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
12 | AFW | 3.1 | 12.366 | 15.466 | 13.566 | 13.566 | 0 | 13.566 | 0% | 12 | AFW | 3.1 | 12.366 | 15.466 | 13.566 | 13.566 | 0 | 13.566 | 0% | 12 | AFW | 3.3 | 0 | 2 | 2 | 5.3 | 3.0997 | 3.0997 | 0% | 0 | 3.0997
13 | BRL | 11.96 | 0 | 11.96 | 8.1 | 8.1 | 0 | 8.1 | 0% | 13 | BRL | 11.96 | 0 | 11.96 | 5.6672 | 5.6672 | 0 | 5.6672 | 0% | 13 | BRL | 11.96 | 11.96 | 0 | -11.96 | 0 | 0 | 0 | 0% | 0 | 0
14 | PRT | 2.793 | 0 | 2.793 | 1.1701 | 1.1701 | 0 | 1.1701 | 0% | 14 | PRT | 2.793 | 0 | 2.793 | 1.1701 | 1.1701 | 0 | 1.1701 | 0% | 14 | PRT | 2.793 | 0.245 | 0 | -0.245 | 2.548 | 2.548 | 2.548 | 0% | 0 | 2.548
15 | SES | 8.866 | 0 | 8.866 | 6.3749 | 6.3749 | 0 | 6.3749 | 0% | 15 | SES | 8.866 | 0 | 8.866 | 0 | 0 | 0 | 0 | 0% | 15 | SES | 8.868 | 0 | 0 | 0 | 8.868 | 8.0574 | 8.0574 | 0% | 0 | 8.0574
16 | SEW | 33.9605 | 0 | 33.9605 | 10.8607 | 10.8607 | 0.30595 | 10.5548 | 2.817% | 16 | SEW | 33.9605 | 0 | 33.9605 | 3.53 | 3.53 | 0.039144 | 3.4909 | 1.109% | 16 | SEW | 33.9605 | 32.64 | 0 | -32.64 | 1.3205 | 1.3092 | 1.3092 | 1.109% | 0.014518 | 1.2947
17 | SSC | 4.1012 | 0 | 4.1012 | 1.8729 | 1.8729 | 0.55998 | 1.3129 | 29.9% | 17 | SSC | 4.1012 | 0 | 4.1012 | 0.37975 | 0.37975 | 0.052203 | 0.32754 | 13.75% | 17 | SSC | 6.4175 | 2.27 | 0 | -2.27 | 4.1475 | 3.8622 | 3.8622 | 8.785% | 0.33931 | 3.5229
| Total | 1146.6001 | -260.7792 | 885.8209 | 566.7197 | 566.7197 | 2.2589 | 564.4608 |  |  | Total | 1146.6001 | -260.7792 | 885.8209 | 394.7987 | 394.7987 | 1.3928 | 393.4059 |  |  | Total | 1208.361 | 550.64 | 14.0137 | -536.6263 | 565.7897 | 344.1254 | 344.1254 | 0.36064 | 2.9392 | 341.1862
Comments
We have overwritten cells L12, L17, L21, L27 and L28 to reflect the allocation between price controls of the investments allowed and not the allocation in April 2019 business plans.

## Deep dive ANH
FD - Deep dive sheet - Anglian Water |  |  |  | DD - Deep dive sheet - Anglian Water |  |  |  | IAP - Deep dive sheet - Anglian Water
Summary at FD |  |  |  | Summary at DD
Company | ANH |  |  | Company | ANH
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 55.6459 |  |  | Totex carried through deep dive AMP7 (£m) | 55.6459
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 55.6459 |  |  | Totex assessed within deep dive (£m) | 55.6459 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 19.0482 |  |  | Totex allowance from deep dive (£m) | 17.082 |  |  | Expenditure carried through deep dive AMP7 (£m) | 22.823
Ofwat view of totex allowance for AMP7 (£m) | 19.0482 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 17.082 |  |  | Ofwat view of allowance for AMP7 (£m) | 15.52
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | Anglian Water accepts our draft determination for most investments. The company has increased the value of some accepted investments without providing an explanation (e.g. single source of supply is now £18.449m instead of £18.338m; power resilience £0.645m instead of £0.642m) and therefore the allowances for the accepted investments are maintained as in the draft determination. The company has made representations on the following investments: • Water treatment works (WTW) resilience: critical shutdown systems and proactive risk visualisation dashboard (£8.142m, instead of the £7.689m requested for draft determinations). These investments were requested in draft determinations as part of various telemetry improvements (dashboards, panels and monitors). The first investment has been identified to reduce the risk of failure of electro-mechanical shutdown panels by replacing all panels with safety integrated level (SIL) rated systems. The company states: "All such shutdown panels are subject to regular testing and inspection but this cannot identify failures that are not age related or predictable so therefore cannot be foreseen or planned for, and is therefore outside management control". The second investment aims to fully implement a risk dashboard at Alton WTW and all other sites where critical asset failure presents a risk to service to customers. The dashboard identifies predictively where, through asset failure or water quality changes, the risk of supply interruptions is increasing." (...) "Utilising our asset criticality models, combined with real time asset performance data and current water quality information, our risk dashboard provides both a current and predicted risk status allowing early intervention to protect the service to customers" (…) “Current capabilities do not allow us to accurately predict these risks to customers and thereby adequately protect them from the consequential risk of loss of supply.” We consider both investments base activities (whether this relates to capital maintenance or to management control activity to assess asset criticality risks) and therefore do not allow them as resilience enhancements. • Critical infrastructure crossings (£2.843m, instead of the £2.842m requested for draft determinations). The company identified 850 high risk infrastructure crossings (including rivers, railways and major trunk roads) that require enhancement to protect customers from significant loss of supply in the event of asset failure. It has prioritised 14 schemes. The company states: “This investment area is not to address maintenance issues but to provide additional protection by duplicating critical assets to protect customers from the impact of unpredictable or premature failures of infrastructure mains which interact with other critical infrastructure.” The company includes an example of a past main burst under a river crossing, exemplifying and quantifying the measures available within management control and the impact to customers in the area. Overall, the investment is accepted as the company provides evidence proportional to the materiality of the scheme that supports the need for investment. The total value of the investment accepted within the need for investment gate for final determinations is £21.823m. | PR19 DD Representation ANH PR19 Supplementary evidence ANH Data Table Commentary | Need for investment | Partial pass | The enhancement investment from WRMP activities allocated by the company to resilience (lines 14 and 53) are reallocated to supply-demand balance enhancement lines (lines 18 and 43): totex £269.508m (capex £264.871m, opex £4.637m). The remaining expenditure belongs to the Resilience Programme: totex £66.777m (£65.105m capex, £1.672m opex). • Emergency response (£11.050m; £10.484m capex and £0.566m opex): The investment is to allow the company to meet SEMD requirements for provision of alternative supplies through tankering and bowsers/bottled water. It is reallocated to SEMD enhancement lines. Emergency preparedness schemes (mobile treatment facilities, securing critical comms, upgrade key & locking systems, CCTV, alarms, etc.) are also reallocated to the SEMD enhancement lines, as these are also part of emergency planning arrangements. Additional reallocations from freeform lines into water resilience lines are: £0.039m (pluvial and fluvial flood protection) and -£0.119m (negative adjustment for third party enhancement spend), which are both accepted. After reallocations, the total expenditure assessed within the water resilience enhancement line is £55.646m which comprises of the following: • Single source of supply risk management (£18.338m; £18.058m capex and £0.280m opex): seven investments to connect isolated communities to a second source of water supply. The investment is accepted as it mitigates the risk to customers only fed from one supply point through interconnecting mains, exploiting synergies with the WRMP strategic inter-connector schemes. • Known water quality challenges (£3.631m; £3.244m capex and £0.387m opex), including: an ultra violet plant (UV) at Covenham Water Treatment Works to mitigate cryptosporidium risk (£2.167m); one investment in the Hartlepool region to dual an existing water main to reduce the risk of customers receiving discoloured water (£0.877m); and enhanced river flow monitoring at one of their reservoirs (£0.587m). These schemes are not allowed under the resilience lines since they address persistent water quality problems that are outside of the scope of resilience enhancements, particularly in terms of the failure modes and probability of the events causing failures or that these are beyond management control. • WTW resilience (£29.674m; £29.389m capex and £0.285m opex), including: telemetry improvements and other related investments (dashboards, panels and monitors) (£12.120m); installations to reduce fire risk in critical electrical panels at 35 sites (£0.419m); upgrading unreliable incoming power supplies at 50 sites (£0.642m); installation of run to waste facilities (£14.061m) and standby dosing lines (£1.374m). The power resilience scheme is accepted, but the other WTW resilience projects are rejected as these relate to either: process failures whose mitigation is within management control, maintenance investments, and site emergency plans that should be in place. • Supply system resilience (£3.940m; £3.930m capex and £0.010m opex): Communications resilience investments to provide communications back-up (£1.098m) are considered to be covered by base funding. The investment to duplicate mains at critical infrastructure crossings (£2.842m) is not sufficiently evidenced to be accepted, particularly regarding key aspects of the risk that the scheme mitigates (i.e. failure mode, probability of failure, consequence for customers and an explanation that these are beyond management control). The total investment passed within the need for investment gate is £18.980m. | PR19 Water Data Tables Commentary (April 2019) Query ANH-DD-CA-004, May 2019 Query ANH-DD-CE-014, May 2019 | Need for investment | Partial pass | The investment line includes as proportion of the investment to support the WRMP supply side strategy (Line 14 = £292.945m capex, Line 53 = £5.006m opex). This includes 16 new strategic potable transfer mains (500km); (2) New WTW (6 Mld) to treat water from Pyewipe WRC for non-household customers; (3) New WTW to supply South Humber Bank customers, and should be considered alongside other parts of the supply and demand programme. The remainder has been assessed under resilience programme (£22.8m capex) consists of activities to mitigate a single source of supply risk to connect isolated communities to a second source of water supply, mobile treatment facilities to provide emergency responses and upgrading unreliable incoming power supplies at five sites which are accepted in this investment line. The other activities, such as maintenance activities to avoid process failure, telemetry upgrades and fire risk for critical panels are regarded as base expenditure. None of the investment in this area relates specifically to protecting assets from flooding risks as per the National Flooding Resilience Review. | PR19 Water Data Tables Commentary, Pp 27 to 29 (WRMP related); Pp 53/54 (resilience prog)
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A
Best option for customers | Partial pass | The total expenditure assessed within the options gate is £21.823m. Because the company has not raised substantive issues in its representation, we retain our draft determination assessment regarding the following investments: • Single source of supply risk management (£18.338m) • Upgrading unreliable incoming power supplies at 50 sites (£0.642m) For the ‘critical infrastructure crossings’ investment (£2.842m) we are applying a 20% optioneering challenge because there is insufficient evidence that the company has considered alternative options to duplicating mains, or that the preferred option has been assessed against the ‘do-nothing’ option. As a result, we pass £2.274m. The total value of the investment accepted within the gate for final determinations is £21.254m. | PR19 DD Representation ANH PR19 Supplementary evidence ANH Data Table Commentary | Best option for customers | Pass | The total expenditure assessed within the options gate is £18.980m which is comprised of the following: - Single source of supply risk management (£18.338m) - Upgrading unreliable incoming power supplies at 50 sites (£0.642m) The company provides additional information regarding its Risk Opportunity and Value (ROV) process to determine the best value options for customers. According to this, "The ROV Process is supported by the Business Impact Matrices (BIMs). The BIMs are designed to monetise risk and link service failures to the resultant cost impact associated with that failure." (...) "This provides a common and consistent framework to assess the value of each option. The selected alternative for each area of investment in this portfolio has been determined through ROV as having the highest equivalent annualised value." (pp. 83-84). The company provides tables with the equivalent annualized costs, benefits and value for each alternative and a general description of the ROV process. The total investment passed within the gate is £18.980m | PR19 Water Data Tables Commentary (April 2019) | Best option for customers | Partial pass | Evidence of detailed customer consultation is presented and indicates strong customer support for measures that increase resilience in water supplies. The company reports "Each scheme has been fully assessed as part of our Risk Opportunity and Value (ROV) process". It is assumed that all schemes put forward in the business plan passed the ROV process even though this is not explicitly stated. This process considers baseline and residual risk of each alternative considered, scored for both private and societal impact. This enables cost benefit analysis to be carried out on each option to choose the best value, lowest whole life cost solution." However the company does not support this statement with examples relating to this enhancement line showing information on alternatives or individual cost/benefits/risk reduction for example. | PR19 Water Data Tables Commentary, Pp 29/30 (WRMP related), Pp 54/55 (resilience prog)
Robustness and efficiency of costs | Fail | Because the company has not raised substantive issues in its representation, we retain our draft determination assessment and apply the company specific challenge to the following investments: • Single source of supply risk management (£16.504m) • Upgrading unreliable incoming power supplies at 50 sites (£0.578m) For the ‘critical infrastructure crossings’ investment (£2.842m) we also apply the company specific efficiency challenge, as the evidence provided by the company remains the same as at draft determination and is not sufficient to demonstrate the robustness and efficiency of costs. As a result, we pass £2.047m for this investment. The total value of the investments accepted within the robustness and efficiency of costs gate is £19.048 m. | PR19 DD Representation ANH PR19 Supplementary evidence ANH Data Table Commentary | Robustness and efficiency of costs | Fail | The total expenditure assessed within the robustness and efficiency of cost gate is £18.980m. The company presents a general view of cost efficiency, stating: "our costs of doing so have been developed using our well populated cost model library that has been developed over several AMPs using data from previously delivered projects, price adjusted to the relevant year. The costs are based on current out turn costs and therefore include embedded efficiencies delivered in AMP6." The company also provides a consultant’s report which benchmarks the capital costs submitted in their plan for various areas, including “sustainable resilient systems” (Appendix 10d, p. 33). The report states that, for a selected set of six projects in the company’s resilience programme, capital costs are on average a 13% lower than those from three other companies. However, the confidence range attached to the cost estimates used as comparators for the benchmarking exercise is +/-12%, which questions the actual cost efficiency of the resilience projects as a whole. As a consequence, a company specific efficiency challenge is applied to the accepted schemes. The total investment passed within the gate is £17.082m | PR19 Water Data Tables Commentary (April 2019) Appendix 10d (September 2018) | Robustness and efficiency of costs | Fail | Detailed cost breakdown is provided to test whether costs are efficient. The company states that "…our costs of doing so have been developed using our well populated cost model library that has been developed over several AMPs using data from previously delivered projects, price adjusted to the relevant year. The costs are based on current out turn costs and therefore include embedded efficiencies delivered in AMP6." As a detailed cost breakdown is not provided and there is insufficient detail on optioneering a 20% efficiency challenge and a further company specific efficiency is applied. | PR19 Water Data Tables Commentary, Pp 30-32 (WRMP related), Pp 56 (resilience prog)
Customer protection | Pass | Because the company has not raised substantive issues in its representation, we retain our assessment regarding the investments allowed at draft determination. The materiality of the additional investment allowed for final determinations is small in comparison to the company's proposed totex within the water network plus and water resources price controls and so customer protection against non-delivery is not imposed. | PR19 DD Representation ANH PR19 Supplementary evidence ANH Data Table Commentary | Customer protection | Pass | The need for customer protection against non-delivery has been assessed for the allowances made. The materiality of the allowed investments is small in comparison to the company's proposed totex within the water network plus and water resources price controls and so customer protection against non-delivery is not imposed. In particular: - Single source of supply risk management: The company does not propose customer protection against non-delivery for this investment, although a reputational PC ('Percentage population with single supply') is reliant on the delivery of this investment. - Upgrading unreliable incoming power supplies at 50 sites: The company does not propose customer protection for this investment. |  | Customer protection | Pass | The company proposes a performance commitment measuring the % of population served by a single source of supply, with a financial ODI for over and under performance if its target and the range of common resilience performance commitments.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A

## Deep dive NES
FD - Deep dive sheet - Northumbrian Water |  |  |  | DD - Deep dive sheet - Northumbrian Water |  |  |  | IAP - Deep dive sheet - Northumbrian Water
Summary at FD |  |  |  | Summary at DD
Company | NES |  |  | Company | NES
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 127.396 |  |  | Totex carried through deep dive AMP7 (£m) | 127.396
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 127.396 |  |  | Totex assessed within deep dive (£m) | 127.396 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 63.7089 |  |  | Totex allowance from deep dive (£m) | 55.7745 |  |  | Expenditure carried through deep dive AMP7 (£m) | 99.987
Ofwat view of totex allowance for AMP7 (£m) | 63.7089 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 55.7745 |  |  | Ofwat view of allowance for AMP7 (£m) | 50.986
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | The company makes representations on our draft determination assessment of this gate for the following investments: • Essex resilience, Abberton-Hanningfield scheme (£20.350m). In its representation the company states that the dissolved air flotation (DAF) treatment at Layer, for which we make an allowance in the raw water deterioration enhancement line, "seeks to restore a level of lost resilience but not increase resilience". The drawing down risk of Hanningfield reservoir described by the company is closely linked to algal and turbidity outages at Layer WTW, or to treatment works maintenance activities that are within management control. We make an allowance to mitigate the risk of algal and turbidity outages through the ‘DAF treatment at Layer’ investment, as part of our assessment of costs to address deterioration in raw water quality. The company mentions other (secondary) risks, but these are not quantified or assessed in the context of Layer water treatment works having a DAF treatment process in place. As a consequence, these are not considered, on their own, sufficient to support the scheme. Further, most of these secondary risks relate to issues outside of the scope of resilience enhancements (i.e. population growth, low rainfall, peak demands) or within management control (e.g. capital maintenance). As a consequence, the investment is rejected in full. • Suffolk resilience (£14.540m). The company has presented additional evidence and specifies that raw water quality issues at River Waveney are the most important source of risk that the investment is mitigating. These are presented as a list of catchment and water quality risks (e.g. agricultural runoff, algae or saline intrusion). According to the company, these are only partially manageable (rated as level 8 in terms of likelihood-consequence) and if a threat arises then Barsham works must depend solely on borehole supplies (these provide a secondary source of supply which is, on itself, insufficient to cover demand). The risk of 37,000 customers losing supply is material and the lack of treated storage implies a low level of mitigation/protection in place. We therefore accept the need for the company to provide 20Ml of treated storage at Barsham treatment works (£10.44m) to reduce customer exposure. The company also proposes mains renewal investments (£4.10m) to expand the transfer capacity between Barsham water treatment works and Ormesby water treatment works to support the latter in the event of the application of an abstraction cessation clause. We reject this last component of the investment as the company provides insufficient evidence to demonstrate that the Ormesby Broad water levels required for the cessation clause to be implemented (i.e. worst historic drought period) are likely to occur in the period assumed by the evidence (the company says that it “is likely that it will be implemented over the next five years”). It is also unclear to what extent the Lound to Gorleston pipeline already mitigates this risk in the short to medium term. As a consequence of the above, the total value of the investment accepted within the need gate for final determinations is £72.390m. | Northumbrian Water Draft Determination - Company Representation 3.3.2 Essex Resilience – Abberton to Hanningfield Transfer Main 3.3.3 Suffolk Resilience 3.3.9 Wearside Resilience Expanded Ofwat query response_NES-DD-CE-007 Query NES-FD-CE-002, September 2019 | Need for investment | Partial pass | The company did not accept our proposed reallocation of the Abberton-Hanningfield raw water transfer scheme (from resilience to supply-demand balance) and has provided additional evidence, which is now assessed under the resilience enhancement lines (totex: £20.35m; capex: £20.35m, opex: £0m). The company has accepted our proposed reallocation of two other schemes (‘Install new UV treatment at Mosswood WTW to manage Kielder crypto risk’ and ‘DAF treatment at Layer WTW’) to the raw water deterioration enhancement lines. Scheme 18 (too critical to fail schemes, £8.340m) is also assessed as part of the resilience enhancement lines, although a component of this investment is linked to emergency response planning and site fencing (totalling £1.460m) and is reallocated to the SEMD enhancement lines. After reallocations, the total expenditure assessed within the water resilience enhancement lines is £127.400m (all capex) which comprises of the following: • The Abberton-Hanningfield scheme (£20.350m) mitigates the same principal risk as the investment for DAF treatment at Layer WTW, which has been reallocated and accepted under raw water deterioration enhancement lines. This means that investment to mitigate algal bloom events has been allowed elsewhere and therefore this is not funded under resilience. The additional (secondary) risks described by the company beyond algal blooms (e.g. those associated with other outages and asset failures) are not considered, on their own, sufficient to support the scheme. • Lartington mains and Tees strategic mains reinforcement (£42.750m): The scheme is partially accepted. The 800mm main from Whorley to Shildon (£19.200m) and the new Shildon WPS (£3.160m) are accepted to provide resilience against single point of failure at Derwent South main. The cross connections at Darlington (£0.210m) are also allowed to provide second source of supply to 18,000 properties. Following the IAP, we have refined the criteria which must be satisfied to demonstrate the need for investment and which are described in the model cover sheet. As a consequence, the +200mm enhancement of the 37.5 km replaced main (£14.080m) is not allowed as there is insufficient evidence of how the additional capacity supports second source of supply improvements in the area, beyond those already allowed and in addition to the renewal of current capacities (i.e. capital maintenance). The service reservoir modifications (£6.100m) are considered part of base investment to improve the operability of the network and are not allowed under resilience enhancements. • Springwell SR and South Tyneside strategic mains reinforcement (£42.580m): The Springwell SR (£16.200m) and link to Carr Hill main (£3.000m) are both accepted to support the 7 km of mains reinforcement (£14.860m), which is allowed to provide second source of supply to properties connected to the Derwent North main. The need for 4km of 1000mm main between Heworth and Pikes Hole plus EOV control (£8.540m) is insufficiently evidenced to provide single point of failure resilience (i.e. failure mode, probability and consequences associated with the risk are poorly defined) and is not allowed. • Barsham SR/WPS and North Suffolk strategic mains (£14.540m): The investment provides strategic treated storage and transfer capacity in North Suffolk and is not accepted, since there is insufficient evidence to define the risks that the scheme is mitigating against (unplanned outage and unprecedented peak demands), particularly regarding the failure modes and probability of the events expected to cause failures and why these are beyond management control. Moreover, the risk of a loss of supply lasting more than three days is not sufficiently evidenced. • Low value-high impact single point of failure schemes (£0.630m): The investment is accepted as these are low materiality projects that address single point of failure at two service reservoirs. • 63 too critical to fail sites (£6.880m after reallocation of £1.460m): The investment is accepted for areas that protect sites against power failure and flood risks (totalling £4.690m). However, elements of the investment that aim to protect against the risk of fire and to conduct surveys are not accepted (£2.190m) as these are considered part of base investments. The total investment passed within the need for investment gate is £61.95m. | Appendix 3.2 (April 2019) Appendix 3.6 (September 2018) Query NES-DD-CA-001, May 2019 Query NES-DD-CE-007, May 2019 | Need for investment | Partial pass | The company have presented 17 schemes within their water resilience enhancement programme - (references are given to the list in the text box below). Of these a total of 3 schemes were reallocated. Scheme 1 was reallocated to Line 8 supply side enhancements as the need was considered to relate to SDB risks. (Appendix 3.2, water resilience, p7). Schemes 2 & 3 (£33m) were reallocated to line 13 investments to address deteriorating raw water quality (Appendix 3.2, water resilience, p7, 22). Scheme 13 & 14 was not accepted as there was insufficient evidence of the specific risk it is expected to resolve. Scheme 15 was also not accepted as it related to utilise existing water resources to protect against outages and this type of known outage risk is seen to be as part of managing existing risk under base costs. Scheme 16) also not accepted as although the risk of a supply interruption at Barsham works is identified, no magnitude or likelihood assessment is provided. It is also not clear how this links with scheme 15) the 4.3km of strategic transfer mains and how this combination provides best value resilience. Further detail should be provided on the risk analysis undertaken looking at the overall resilience of properties served by Ormesby, Lound and Barsham WTWs and how the proposed schemes provide the best option. The analysis should identify that the schemes provide resilience against low probability, high magnitude events. Scheme 17 was not accepted it is not clear which of the risks identified in the central catchment this additional storage is targeted at and why 2 - 3 days is an appropriate amount. . Without further detail and evidence on the nature of the risk of failure at Mosswood or the Derwent North main the spend cannot be justified under enhanced resilience expenditure. | Appendix 3.2, water resilience, p6-9. Appendix 3.2, water resilience, p22-24 Appendix 3.2, water resilience, p22-F29
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A | NA | NA
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A | NA | NA
Best option for customers | Partial pass | The total expenditure assessed within the options gate is £72.390m. The company has not raised substantive issues and we retain our draft determination decisions for the following investments: • Lartington mains and Tees strategic mains reinforcement (£22.570m); • Low value-high impact single point of failure schemes (£0.630m); and • 63 too critical to fail sites (£4.690m). The company makes a representation in relation to the optioneering challenge applied to the service reservoir component (£16.200m) of the Wearside resilience scheme (Springwell SR and South Tyneside strategic mains reinforcement). The company provides additional evidence to explain that spare capacity (62Ml instead of the 42.75Ml identified as required in the business case) is needed given the risk of hazardous ground conditions affecting storage capacity in the area, which could potentially impact on 54Ml of existing strategic storage. The company mentions past events where storage capacity has been reduced as a result of ground movement in the area. Although the company states that the additional capacity is not linked to asset condition, it also states: “the need to replace existing reservoir capacity is sufficiently pressing, bearing in mind that Entec’s study of 2010 recommended decommissioning some storage sites by 2025”. We consider that the risk posed by hazardous ground conditions in parts of the Wearside area is not sufficiently defined and any additional capacity provides an asset health benefit to storage reservoirs in the area, which is covered by the allowance for base expenditure. We therefore maintain our draft determination decision on this investment and apply a 20% optioneering challenge to the service reservoir element (i.e. we allow £12.96m). As a result, the total allowance for this scheme remains as in the daft determination: • Springwell SR and South Tyneside strategic mains reinforcement (£30.820m). Regarding the Suffolk resilience investment (£10.44m), the company considers a number of options, but these are reduced to implementing variations on the same solution (different capacities or elements involved). The company does not provide alternatives to treated storage (e.g. support from other treatment works, source control mitigations, etc.) We therefore apply a 20% optioneering challenge to this investment, making an allowance of £8.352m within this gate for this investment. The total value of the investment accepted within the gate for final determinations is £67.062m. | Northumbrian Water Draft Determination - Company Representation 3.3.2 Essex Resilience – Abberton to Hanningfield Transfer Main 3.3.3 Suffolk Resilience 3.3.9 Wearside Resilience Expanded Ofwat query response_NES-DD-CE-007 Query NES-FD-CE-002, September 2019 | Best option for customers | Partial pass | The total expenditure assessed within the options gate is £61.95m which is comprised of the following: - Lartington mains and Tees strategic mains reinforcement (£22.570m); - Springwell SR and South Tyneside strategic mains reinforcement (£34.060m, reduced to £30.820m after optioneering challenge detailed below); - Low value-high impact single point of failure schemes (£0.630m); and - 63 too critical to fail sites (£4.690m). Most schemes presented by the company consider a range of options, including: descriptions of alternatives (including do-nothing), the cost of each alternative, and a description of the benefits attached to each alternative in reducing risk exposure. Although the company sufficiently evidences the need to invest in the Springwell service reservoir it does not not clearly justify its 62Ml capacity, as different capacities are not included in the optioneering matrices. The initial revised storage requirement is presented as 42.75Ml (accounting for peak demand conditions) but the company states that this "leaves a significant residual risk of failure on the 3 km stretch of main which would become the outlet of Springwell reservoir". To address this residual risk (which is not discussed nor quantified), an option of a 62Ml storage with duplicated outlet is selected; however, the company does not consider a smaller reservoir with duplicated outlet to mitigate against this residual risk. A 20% cost challenge is therefore applied to this part of the investment (£16.20m). The total investment passed within the gate is £58.71m. | Appendix 3.2 (April 2019) Appendix 3.6 (September 2018) | Best option for customers | Partial pass | Schemes 4, 5 & 6 were accepted in full as the schemes resolve single source of supply risks at large urban centres with relatively low cost interventions. Further likelihood of failure analysis would have provided a stronger evidence of criticality of the investment. Schemes 7 to 12 were accepted. The company did identify a need for these schemes but because of the scale of the proposed schemes the evidence to support the need is considered insufficient. Further details of analysis undertaken to understand likelihood of failures and likely duration of failures for these schemes would need to provide a stronger case for schemes proposed. As a result an efficiency challenge was applied (20%). There was also very limited evidence of any optioneering being presented or alternative options being considered. The company state that "technical options for most schemes were often limited as we needed to address a specific risk, be it lack of water transfer capacity or emerging water quality issues." (Appendix 3.2, water resilience, p9) | Appendix 2.2, p153.
Robustness and efficiency of costs | Fail | Because the company has not raised substantive issues in its representation, we retain our draft determination assessment and apply the company specific challenge to the following schemes: • Lartington mains and Tees strategic mains reinforcement (£21.442m); • Low value-high impact single point of failure schemes (£0.599m); • 63 too critical to fail sites (£4.456m); and • Springwell SR and South Tyneside strategic mains reinforcement (£29.279m). For the Suffolk resilience investment (£8.352m), we consider that the company does not provide evidence that demonstrates the robustness and efficiency of the resilient investments. Therefore we apply the company specific efficiency challenge to this investment and pass £7.934m. The total value of the investment accepted within the gate for final determinations is £63.709m. | Northumbrian Water Draft Determination - Company Representation 3.3.2 Essex Resilience – Abberton to Hanningfield Transfer Main 3.3.3 Suffolk Resilience 3.3.9 Wearside Resilience Expanded Ofwat query response_NES-DD-CE-007 Query NES-FD-CE-002, September 2019 | Robustness and efficiency of costs | Fail | The total expenditure assessed within the robustness and efficiency of costs gate is £58.71m. The company describes at a high level the methods that it has used to develop efficient and robust costs, and states that cost benchmarking has been carried out by consultants, but it does not provide any evidence that demonstrates the robustness and efficiency of these specific investments. Therefore we apply the company specific efficiency challenge to the allowances made. The total investment passed within the gate is £55.77m. | Appendix 3.2 (April 2019) Appendix 3.6 (September 2018) | Robustness and efficiency of costs | Fail | There was no detailed evidence found on scheme costs, therefore it was not possible to judge cost efficiencies of these schemes in detail. A company specific efficiency challenge was applied. | Appendix 3.2, water resilience, p9-10.
Customer protection | Pass | The need for customer protection against non-delivery has been assessed for the allowed schemes (including the Suffolk resilience investment accepted in our draft determination). As in draft determination, this is covered by a bespoke performance commitment that monitors the delivery of the resilience programme for water (‘Delivery of water resilience enhancement programme’). The PC has an underperformance ODI attached to it, which protects costumers from the company not delivering the accepted schemes. The customer protection is appropriate. | Northumbrian Water Draft Determination - Company Representation 3.3.2 Essex Resilience – Abberton to Hanningfield Transfer Main 3.3.3 Suffolk Resilience 3.3.9 Wearside Resilience Expanded Ofwat query response_NES-DD-CE-007 Query NES-FD-CE-002, September 2019 | Customer protection | Pass | The need for customer protection against non-delivery has been assessed for the allowed schemes. This is covered by a bespoke performance commitment that monitors the delivery of the resilience programme for water (‘Delivery of water resilience enhancement programme’). The PC has an underperformance ODI attached to it, which protects costumers from the company not delivering the accepted schemes. The customer protection is appropriate. |  | Customer protection | Partial pass | Along with the common resilience PCs the water resilience enhancement programme is covered by a performance commitment with a penalty only ODI to protect customers against late or non-delivery of the overall resilience programme.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A | NA | NA
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A | NA | NA
Further analysis / arguments
Water resilience schemes after reallocations to other lines Requested (£m) Allowed (£m)
1) Batch 1: Abberton to Hanningfield RW transfer main at 50 Mld capacity Reallocated
2) Batch 1: Install new UV treatment at Mosswood WTW to manage Kielder crypto risk Reallocated
3) Batch 1: DAF treatment at Layer WTW Reallocated
4) Batch 1a: Cross connections into C60/60a for Darlington 0.21 0.21
5) Batch 1: 315m of 700mm main to duplicate Chirton SR outlet main 0.40 0.40
6) Batch 2: 30m of 900mm main @Herongate SR 0.23 0.23
7) Batch 1a: Replace 37.5km of 600mm with single 800mm St main 14.08 11.26
8) Batch 1c: 16km of 800mm main from Whorley to Shildon [link to Batch 2 - Central] 19.20 15.36
9) Batch 1: 1.5km of 600mm main Carr Hill Link to Springwell SR 3.00 2.40
10) Batch 1: 7km of 1000 mm main from Springwell to Pikes Hole plus EOV control 14.86 11.89
11) Batch 1: 4km of 1000mm main between Heworth and Pikes Hole plus EOV control 8.52 6.82
12) Batch 2: New 55Ml WPS at Shildon SR [Link to Batch 1c - Tees] 2.86 2.29
13) Batch 1b: New inlet/outlet arrangement at Maltby SR (6km 800mm main) 5.40 0
14) Batch 2: Mods to Ormesby WPS and abandon 3 SRs 0.70 0
15) Batch 1: Enabling mains schemes at North Cove and S Lowestoft 4.10 0
16) Batch 2: New treated water storage and WPS. 10.14 0
17) Batch 1: Springwell SR - 62Ml capacity 16.20 0
Total Requested (excluding reallocations to other lines) 99.90 50.86

## Deep dive WSH
FD - Deep dive sheet - Dŵr Cymru |  |  |  | DD - Deep dive sheet - Dŵr Cymru |  |  |  | IAP - Deep dive sheet - Dŵr Cymru
Summary at FD |  |  |  | Summary at DD
Company | WSH |  |  | Company | WSH
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 113.886 |  |  | Totex carried through deep dive AMP7 (£m) | 113.886
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 113.886 |  |  | Totex assessed within deep dive (£m) | 113.886 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 18.7401 |  |  | Totex allowance from deep dive (£m) | 3.61 |  |  | Expenditure carried through deep dive AMP7 (£m) | 38.427
Ofwat view of totex allowance for AMP7 (£m) | 18.7401 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 3.61 |  |  | Ofwat view of allowance for AMP7 (£m) | 5.31
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | Dŵr Cymru accepts our draft determination for most investments, including the allowance made for the ‘Network resilience schemes’ investment. However, the company makes representations on the following investments (total value of £33.509m): • Extending our South Wales grid (£19.908m). The company provides additional evidence to support the need for this investment to mitigate risks in its Tywi Conjunctive Use System (TCUS) and South East Wales Conjunctive Use System (SEWCUS). The company identifies two main risk scenarios that could impact supply (i.e. trunk main failures and service reservoir bacteriological failure). The justification for the investment has improved in terms of the assessment of potential trunk main failures in the network and its explanation of current management control measures. As a result, the investment is passed for the risk of trunk failures from Tongwynlais. On the other hand, the bacteriological risk is closely related to service reservoir maintenance and inspection issues to control structural defects and prevent potential ingress and, therefore, we consider it is within management control and outside of the scope of resilience enhancements. In addition, the need for a bidirectional main is also explained in the company’s response to our query (i.e. possible failure to supply to Cefn Hirgoed service reservoir from the single 40” main); however, the consequence to customers and the management control measures under failure scenarios in the TCUS network are not evidenced as to demonstrate that the need to mitigate failures in this network is beyond management control. Given we acknowledge the first risk scenario, we pass the investment to mitigate trunk main failures from Tongwynlais. • Hereford supply resilience (£13.601m). The company provides additional evidence to support the need for this investment. The company raises a number of risks that could cause outages beyond 24 hours (i.e. fire, malicious damage and pollution). The risks the company describes which potentially cause outages beyond 24 hours are either: related to other cost areas for which we already make an allowance (e.g. SEMD enhancements or base costs); or not sufficiently evidenced with a thorough risk appraisal. We are concerned that the company provides insufficient evidence of considering alternative pollution control options to mitigate the identified risks. In this sense, the company acknowledges that its proposal to provide 48h treated storage is a short to medium term solution and it is a temporary solution inappropriate for the long-term. As a consequence, we do not pass the investment through this gate. For us to have made an allowance the company should have undertaken a thorough strategic resilience assessment for Hereford water supply to consider how to improve its resilience. The total value of the investment that we accept within the need gate for final determinations is £23.708m. | PR19 DD WSH.DD.CE.4 Extending Our South Wales Grid PR19 DD WSH.DD.CE.5 Hereford Water Supply Resilience Query WSH-FD-CE-001, September 2019 | Need for investment | Partial pass | The company has reallocated the following investments in line with our IAP feedback (£30.390m compared to our recommended £40.010m), including: • Vowchurch from line 14 (Resilience) to line 8 (Supply side enhancements) (£5.990m: £5.830m capex, £0.160m opex); • Brecon Beacons mega-catchment from line 14 (Resilience) to line 13 (Raw water deterioration) (£9.000m); and • NEP Catchments from line 14 (Resilience) to line 17 (Drinking Water Protected Areas); (£15.400m). The WS10 scheme (‘A range of projects to improve emergency planning capability’) to optimise tanker base locations and other emergency equipment (£0.541m) is considered to be part of SEMD investment and has been reallocated accordingly. Dŵr Cymru includes adjustments for the principal use of assets within its capital expenditure proposals (£10.044m). Under principal use, capital expenditure should be wholly reported within the business unit that principally uses the associated assets. We would expect to see principal use recharges only within operating expenditure. Furthermore, to consider a principal use adjustment we require the company to provide information on the activities that are shared between business units and the basis for the proportion of the expenditure that is allocated to another business unit. We have therefore not included principal use adjustments within our assessment. After reallocations, the total expenditure assessed within the water resilience enhancement lines is £103.840m which comprises of the following: • Investment WS1 (‘Installation of contact tank cleaning assets at water treatment sites’) (£10.180m): The investment is not allowed under the resilience enhancement line as this is related to the company not meeting the latest standards that would allow it to maintain its assets, for which the company receives a base implicit allowance. • Investment WS2 (‘Improving Felindre WTW quality resilience (60%)’) (£2.703m): This investment addresses sludge storage space constraints on site derived from poor raw water quality events, which could reduce the treated water output. This is considered a risk which has consequences within management control and is not accepted as a resilience enhancement. • Investment WS3 (‘Capel Curig WTW abandonment’) (£2.101m): The investment addresses the consequences of extreme weather events (high temperatures and heavy snow) that deteriorate raw water quality and limit the ability of the WTW to treat water to an acceptable quality. However, the evidence suggests that the root cause of the problem is an inappropriate primary treatment process that is inefficient at dealing with organic compounds present in raw water and causes a chronic issue at the site. As a consequence, the investment is not accepted in the resilience line as the company provides insufficient evidence of the failure mode and probability associated to these weather events, and why the consequences of these are beyond management control. • Investment WS4 (‘Network Resilience schemes’) (£5.308m) are partially accepted (£3.800m), including: ‘Bwlch Tunnel Bypass, Alwen Trunk Main’ (£3.000m) to mitigate against tunnel failures; and ‘Additional Main at the River Usk Crossing at Priory Wood’ (£0.800m) as it removes the risk of single sources of supply at crossing points which can be difficult to recover and respond from quickly. Based on the new evidence provided by the company and on the revised criteria developed following IAP and companies’ responses, the remaining investments are rejected because they address issues for which the company receives an implicit base allowance to address: capacity limitations (‘Improved cross connections within the Rhiwbina system’) and solving frequent interruptions to supply (‘Duplicate crossing of the Llangunnor main’). • Investment WS5 (‘Post tensioned concrete tanks replacement’) (£13.581m): The scheme is rejected as it focuses on replacing service reservoirs at risk of catastrophic failure due to their structural integrity, which is an asset health issue for which the company receives a base implicit allowance. • Investment WS6 (‘Extending our south Wales grid’) (£19.908m): The scheme connects the South East Wales Conjunctive Use System and the Tywi Conjunctive Use System to provide bi-directional transfer capability (30Ml/d) from West to East. The company fails to demonstrate the specific risks that it is trying to address through this investment (other than general comments around "failures of mains, failure of treatment works and extreme weather events") and how the risks are beyond management control (for example the company states that "the likelihood of a failure in these zones is currently minimised through our operational and event management processes, but a significant residual risk remains”; however, there is no evidence of the levels of risk that the scheme mitigates against). • Investment WS7 (‘Hereford water supply resilience’) (£13.601m): The scheme addresses treatment issues at Broomy Hill WTW due to raw water quality fluctuations on River Wye after extreme rainfall events. The investment is not accepted as the company does not evidence the risk that the scheme is mitigating against in terms of the likelihood of these events or how process failures (namely automated coagulant dosing not performing well across the range of raw water quality conditions) are beyond management control. It also fails to explain what type of events would cause failures beyond 24 hours. • Investment WS8 (‘Critical trunk mains assessments’) (£3.627m): This investment is not allowed within the resilience enhancement lines as it relates to carrying out risk assessments for critical mains, an activity for which the company receives a base implicit allowance. • Investment WS9 (‘Additional storage at Llwynypia Quarry tanks’) (£3.229m): The scheme focuses on replacing service tanks to provide additional supply redundancy to the system under drought and asset failure conditions. These schemes are considered part of capital maintenance and should be funded through the company’s base allowance. • Investment WS11 (‘IS projects to provide greater resilience’) (increased from £9.34m in the IAP to £29.602m): The company has enlarged the scheme with a capital expenditure reallocation from retail (£20.3m). The company provides new evidence indicating that the purpose is to "fundamentally improving our underlying [IT] infrastructure and our analytics capabilities”. This includes the implementation of real-time monitoring, integration of IT and operational data collection, and testing and robotic process automations. Unlike during the IAP, the scheme is not reallocated to SEMD lines, given the additional evidence. We consider these activities to be part of base investment to improve analytical processes and reject them within the resilience enhancement lines. The total investment passed within the need for investment gate is £3.800m. | B3.B Data tables changes 1 April 2019 WSH B3.A.4 Welsh Water Services Table Commentaries WS WN WR April 2019 B2.11.WSH.CE.A1 Water Resilience IAP Response B3.A.2 Welsh Water Retail Tables Commentaries April 2019 Query WSH-DD-CE-009, May 2019 | Need for investment | Partial pass | Overall WSH have presented 11 schemes within their resilience enhancement line. It should be noted that the costs presented within the business plan data tables relating to line 14 and those in the enhancement cases do not appear to align exactly and therefore best efforts have been made to align the scheme costs between these 2 sources. 5 schemes totalling £41.01m were reallocated as the need they resolved were related to other investment areas. These include: 1) Phase 1 delivery of improvements for the development of the Brecon Beacons Mega catchment (£9m) reallocated to Line 18 raw water deterioration. (5.8A - Water Resources, p22) 2) Improved interconnectivity between Herefordshire and Vowchurch WRZ to provide 1-200 drought resilience. (£5.83m) reallocated to Line 8 - SDB measure as the need was associated with providing drought resilience to the Vowchurch WRZ. 3) Water resource safeguard zones (£16.3m) reallocated to Line 18 as measures relate to either raw water deterioration or to Line 17 Drinking Water Protected Areas. The schemes consists of 23 safeguard zones 1 of which is included within WINEP3 but the other 22 are still awaiting confirmation. 4) Improvements to emergency response to provide capability to comply with SEMD (£0.54m) 5) Improvements to IS and cyber security (£9.34m) investment was reallocated to Non-SEMD enhancements. Schemes 6,7,8,9 and 10 were not sufficiently evidenced as relating to low probability-high consequence risk and better considered as base investment. Scheme 11) the Network Resilience schemes (£5.31m) was accepted it removes the risk of single sources of supply at crossing points which can be difficult to recover and respond from quickly. . These schemes include: - Bwlch Tunnel Bypass, Alwen Trunk Main (£3m) - Improved Cross Connections within the Rhiwbina system (£1m) - Additional Main at the River Usk Crossing at Priory Wood (£0.76m) - Duplicate Crossing of the Llangunnor Main (£0.8m) | 5.8A - Water Resources 5.8F PR19 IC Water Quality WSH 5.8H PR19 Customer Minutes Lost Service Improvement 1.2 Welsh Water Services Table Commentaries WS WN WR, p15-16
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A
Best option for customers | Partial pass | The total expenditure assessed within the options gate is £23.708m. The company has not raised substantive issues in its representation regarding the ‘Network resilience schemes’ investment (£3.800m) and we retain our draft determination assessment regarding this investment. For the ‘Extending our South Wales grid’ investment (£19.908m) we apply a 20% optioneering challenge because the company provides a limited view of options that compares costs and benefits (i.e. do-nothing and two versions of the same interconnector). Other options are briefly discussed (e.g. dual mains at critical crossings) in response to our query to the company, but these are early dismissed by the company in the selection process without providing enough information to assess options that mitigate individual risks. As a result, we pass £15.926m for this investment. The total value of the investment accepted within the gate for final determinations is £19.726m. | PR19 DD WSH.DD.CE.4 Extending Our South Wales Grid PR19 DD WSH.DD.CE.5 Hereford Water Supply Resilience Query WSH-FD-CE-001, September 2019 | Best option for customers | Pass | The total expenditure assessed within the options gate is £3.800m which is comprised of the following: • Scheme WS4 (‘Network Resilience schemes’): ‘Bwlch Tunnel Bypass, Alwen Trunk Main’ (£3.000m) to mitigate against tunnel failures; and ‘Additional Main at the River Usk Crossing at Priory Wood’ (£0.800m) as it removes the risk of single sources of supply at crossing points which can be difficult to recover and respond from quickly. The new evidence provided by the company discussed a number of options for each scheme, including the do-nothing (reactive) option. Costs are provided for each alternative and benefits briefly explained, which allow to select the best option in each case and seem appropriate for the materiality of the accepted investments. The total investment passed within the gate is £3.800m. | B2.11.WSH.CE.A1 Water Resilience IAP Response | Best option for customers | Partial pass | The company provides some evidence of considerations of alternative options, but this is limited to: Do nothing - defer investments to AMP8, Maintain current levels of service and meet legal obligations & Integrated intervention programme with enhancement (5.8A - Water Resources, p13). The chosen option is the Integrated intervention programme with enhancement because "it is the most effective way to deliver interruption to supply benefits and improve our service standards for our customers during AMP7. These improvements are supported by our customers and were captured during our customer consultation process." (5.8A - Water Resources, p13) The company has provided limited evidence of its customer research, where it has presented customer WtP research across different lengths of service interruptions to demonstrate that customers place a high value on interventions to improve reliability of supply. (5.8A - Water Resources, Table 2, p6) | (5.8A - Water Resources, Table 2, p6)
Robustness and efficiency of costs | Fail | Because the company has not raised substantive issues in its representation, we retain our draft determination assessment and apply the company specific challenge to the ‘Network resilience schemes’ investment (£3.610m). For the ‘Extending our South Wales grid’ investment (£15.926m) the company does not provide additional evidence and we maintain our draft determination assessment. We consider there is insufficient evidence of how these costs compare to any industry benchmarks and, in particular, to demonstrate the efficiency and robustness of specific resilience enhancement investments. As a result, we apply a company specific efficiency challenge and pass £15.130m for this investment. The total value of the investment accepted within the gate for final determinations is £18.740m. | PR19 DD WSH.DD.CE.4 Extending Our South Wales Grid PR19 DD WSH.DD.CE.5 Hereford Water Supply Resilience Query WSH-FD-CE-001, September 2019 | Robustness and efficiency of costs | Fail | The total expenditure assessed within the robustness and efficiency of cost gate is £3.800m. The company provides a general document regarding cost efficiency and benchmarking, stating: "By starting early on this process, we have been able to identify very significant potential cost savings, in all aspects of our activities. If fully delivered as planned, these savings total around 10% of Totex over the AMP7 period, with an ongoing saving of over 12% a year being achieved in 2024-25." (p. 4). However, there is insufficient evidence of how these costs compare to any industry benchmarks and, in particular, to demonstrate the efficiency and robustness of specific resilience enhancement investments. The company specific cost efficiency challenge has been applied to investments for which allowances are made. The total investment passed within the gate is £3.610m. | 3.6 PR19 Costs efficiency, benchmarking and recovery WSH B2.11.WSH.CE.A1 Water Resilience IAP Response | Robustness and efficiency of costs | Partial pass | The company also included a risk allowance of £9m. There is no evidence to support this and risk is covered by WACC so this has been removed. | (5.8A - Water Resources, p13)
Customer protection | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | PR19 DD WSH.DD.CE.4 Extending Our South Wales Grid PR19 DD WSH.DD.CE.5 Hereford Water Supply Resilience Query WSH-FD-CE-001, September 2019 | Customer protection | Pass | The need for customer protection against non-delivery has been assessed for the allowed schemes. The materiality of the allowed investment is small in comparison to the company's proposed totex within the water network plus and water resources price controls and so customer protection against non-delivery is not imposed. |  | Customer protection | Pass | The company includes the range of common resilience and asset health PCs designed to incentivise resilience. The company also has proposed bespoke PCs measuring a critical asset resilience score for above and below ground water assets. The company has not proposed a specific PC associated with the delivery of the resilience enhancements, given the scale of the allowed investment this is considered appropriate.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A
tbc - covers various schemes

## Deep Dive TMS
FD - Deep dive sheet - Thames Water |  |  |  | DD - Deep dive sheet - Thames Water |  |  |  | IAP - Deep dive sheet - Thames Water
Summary at FD |  |  |  | Summary at DD
Company | TMS |  |  | Company | TMS
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 204.8924 |  |  | Totex carried through deep dive AMP7 (£m) | 204.8924
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 204.8924 |  |  | Totex assessed within deep dive (£m) | 204.8924 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 197.3541 | For final determination we allow an additional £179.8m for the London Water Supply resilience scheme. For our decision regarding the London Water Supply resilience scheme see ‘PR19 final determinations: Thames Water – cost efficiency additional information appendix’. |  | Totex allowance from deep dive (£m) | 73.6888 |  |  | Expenditure carried through deep dive AMP7 (£m) | 208.7774
Ofwat view of totex allowance for AMP7 (£m) | 197.3541 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 73.6888 |  |  | Ofwat view of allowance for AMP7 (£m) | 109.8858
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | The company accepts our draft determination for power resilience for water sites and we pass £23.400m within the need gate. For our decision regarding the London Water Supply resilience scheme see ‘PR19 final determinations: Thames Water – cost efficiency additional information appendix’. | TW-DD-001-Thames Water Response to Ofwat’s PR19 Draft Determination TW-DD-A04 - NEL supply resilience enhancement case | Need for investment | Partial pass | The total expenditure requested within the water resilience enhancement lines is £204.892m; however, this figure differs from the investments detailed in the business plan resilience narrative provided in the April 2019 submission (£203.2m). Our allowances are based on this last figure, which comprises of the following: London Resilience Scheme AMP7 total requested investment is £179.800m, as at the IAP stage, although new evidence has been presented as part of the April 2019 submission. Additional works covering AMP8 to AMP11 are referenced with a value of ~£1.3bn. The requested investment in AMP7 is a part of a long-term plan to improve the resilience of London's water supply. North East London is considered to be the area of greatest risk for the company. The proposed investment consists of three elements: • Mitigate the impact of increasing levels of algae in raw water to Coppermills WTW (£49.5m AMP7); • Commission an alternative high-lift pumping station to that existing to remove this single point of failure and make necessary network reinforcements (£13.0m AMP7 & £43.5m AMP8); and • Initial works to mitigate hazards leading to the loss of the entire Coppermills WTW site (£117.3m AMP7 & £135.3m AMP8). The need for these three investment elements is assessed as follows, allowing investments to mitigate risks associated with increasing levels of algae (£49.5m) and with single point of failure at the high-lift pumping station (£13.0m): • Increasing levels of algae in raw water to Coppermills WTW. Thames Water states that the water quality in its raw water reservoirs is deteriorating (Fig 16, p. 45), although the company should make clear that the evidence presented relates to reservoirs serving Coppermills WTW. The company states climate change as the cause and that its management strategies are not effective when the levels in the reservoirs are low, thus implying it has to operate reservoirs at these low levels and the levels of algae are beyond management control. There is no further supporting evidence to confirm company actions, for example optimising abstractions, nor how this risk will change in the future. • Failure of the high lift pumping station (HLPS). Thames Water identifies the HLPS at Coppermills WTW as a critical asset with a common manifold that is a single point of failure. The manifold is a steel pipe encased in concrete and TMS states that it is not possible to inspect the asset and thus its condition is unknowable. Thames Water states there will be a supply deficit in NE London should the HLPS fail, which demonstrates that failure would result in a high consequence event. The company states that it has a deterioration model of the asset but has not presented any details of it. • Loss of entire output of Coppermills WTW. The company identifies multiple hazards capable of leading to the loss of the entire site output. These include a de-railed train, major fire, earthquake, aircraft crash, fluvial flooding, etc (table 12, p. 58). It is recognised that the consequence of failure of the entire site would be very significant. However, the company does not present this risk in the context of a company-wide risk management process and thus has not presented sufficient evidence that, above all other risks it is facing this is a priority considering the likelihood of these events. The company has not illustrated how the current proposed plan represents the best value to customers overall considering proposed future investment across London and elsewhere. As London can be considered a single supply zone (p. 17) there will be interactions between the risks in different areas resulting in different investment plans having different cost-risk profiles over time. Schedule B, however, does set out some capability to examine these wider concerns. The company seeks to manage this uncertainty through their 'investment wrapper' approach creating a working group that agrees scope/revenue limits at circa end 2022. This element of the investment is material (£252.000m over AMP7 & 8) and as such there is an expectation of appropriate level of supporting evidence. As a result, this lack of supporting evidence results in the need for investment not being accepted. Power resilience for water sites The need for the investment (£21.100m capex and £2.300m opex; £23.400m totex) is accepted in the resilience lines. The investment protects 31 water sites against the risk of power supply interruptions and disturbances. The company cites evidence that risk of widespread power outage is rising and describes a risk assessment and prioritisation exercise it has conducted in order to define the sites for investment during AMP7. The total investment passed within the need for investment gate is £85.900m (£62.5m from the NE London Resilience scheme and £23.4m from the Power Resilience scheme). | TW-CE_A7. Delivering long-term system resilience for London's water supply. TW-CE-A12 Resilience (excluding North East London water supply system). Query TMS-DD-CA-004, May 2019 Query TMS-DD-CE-013, May 2019 | Need for investment | Pass | The majority of this claim relates to the North-East London Resilience Scheme (£179.7m). The remaining investment is £24.6m totex (£21.1m capex, £3.5m opex) for improving power resilience at 31 sites and £8m totex (£8m capex, zero opex) for improving flooding resilience at 25 sites. Resilience expenditure is expected to be related to low probability-high consequence events that would not be considered as part of routine operations and thus this investment is appropriate to this line and the need is accepted. However as set out below we are concerned that the North-East London Resilience Scheme is not fully integrated into the company supply-demand strategy and that as the scheme specification progresses we will seek clarity on this. There are two elements to the North-East London Resilience Scheme relating to Coppermills WTW. 1.) Failure of the high lift pumping station (HLPS). Thames Water identifies the HLPS at Coppermills WTW as a critical asset. It has a common inlet and outlet manifold and thus is a single point of failure (1. s3.59). The manifold is a steel pipe encased in concrete and TMS states that whilst it has been assessed it has not been inspected (1. s3.59). The company estimates an annual probability of failure at 1 in 50 years although it is not clear what was assessed, nor how this figure was arrived at (1. s3.59). It would be helpful to understand the sensitivity of this value in identifying this as the most critical resilience risk in the company. Thames Water states there will be a supply deficit in NE London and also issues on the Coppermills site should the HLPS fail (1. s3.60 to s3.62). Therefore it would appear that a ‘safe to fail’ option is inappropriate without further mitigations and any intervention should address this. The supply deficit is estimated as 520 ML/d, i.e. the loss of Coppermills and transfer from the London ring main (TWRM). This risk is consistent with our expectations in terms of resilience related investment, i.e. it addresses a low probability – high consequence event. 2.) Reduction in site output during episodes of algal blooms. Thames Water states that the water quality in its raw water reservoirs is deteriorating (1. s3.63). It states that its management strategies are not effective when the levels in the reservoirs are low (s3.65) and implies it operates reservoirs consistently at these low levels and thus the levels of algae are beyond management control. Thames Water presents a graph (1. Fig 8, pg 21) sourced from its dWRMP and it is not clear if the proposed intervention is also accounted for under its source deployable outputs. The information is insufficient to confirm the company is doing everything to manage this issue nor how this risk will change in the future. TMS state that the impact of the algal bloom is a loss of deployable output and increasing operational cost (1. s3.66). It states a worst case scenario of the algal bloom coinciding with one at works in West London (with a probability of 1 in 25 years) so will not be able to make up all the supply deficit (1. s3.67). Thames has not clearly stated the impact on the deployable output of Coppermills under a range of likely scenarios. It states that the reduced output due to algal blooms from Coppermills WTW results in a supply deficit of 391 ML/d (1. s3.70) in NE London. However table 4 (pg 22) shows that the output of Coppermills WTW will reduce by only 150ML/d as a result of an algal bloom. Therefore this issue seems linked to a broader question relating to the supply-demand balance across this zone. Considering water available from other sources, the overall deficit is estimated as 208 ML/d. There are also significant population growth predictions for London and the company further states it has a peak water production deficit and network transmission constraints (1. s3.72). In summary this risk does not fit easily within the definition of a resilience scheme on the basis that the probability of the single event is high. In addition it needs to be confirmed if these production losses are also accounted for in the WRMP. Notwithstanding the intervention has been assessed further. | 1. CSD006-WNP-04b-PR19-FE. Delivering long term system resilience for the London water supply. 2. DT02 PR19 Data Tables Commentary, Section 5.1, page 65 (brief mention). 3. Flood resilience: PCD5-PR19-Water Network Plus, Section 3.5.72, page 87. 4. Power resilience: PCD5-PR19-Water Network Plus, Section 3.5.70, page 86.
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A
Best option for customers | Partial pass | The company has raised no substantive issues in its representation regarding the power resilience investment and we retain our draft determination 20% optioneering challenge for this investment, passing £18.720m. For our decision regarding the London Water Supply resilience scheme see ‘PR19 final determinations: Thames Water – cost efficiency additional information appendix’. | TW-DD-001-Thames Water Response to Ofwat’s PR19 Draft Determination TW-DD-A04 - NEL supply resilience enhancement case | Best option for customers | Partial pass | The total expenditure assessed within the options gate is £85.900m which is comprised of the following: London Resilience Scheme (£62.5m) The company presents a qualitative description of its appraisal of different solution options including regional water transfers. The output of quantitative cost-benefit analyses is summarised in tables but the underlying detail is not presented. The company does not expect final engineering design, etc. to be complete until 2021 (p. 8) and advises the options are 'provisional' or at the 'strategic option stage' (p. 37), however the supporting text of options appraisal discounts the other options, which seems premature. Table 13 gives the B-C Ratio for algal treatment as 36, HLPS as 39 and the new works as 2. This assessment is completed on the basis the WRMP is delivered in full (p. 64). Increasing levels of algae. There is evidence that the company considered a range of options including treatment within the reservoir but its preferred solution is to commission a Mecana pile cloth filter unit to treat 200 ML/d of the 539 ML/d site capacity (deployable output) to reduce the peak load of algae. The company has confirmed in response to a query that the works for this AMP are not in West London (pp. 4 and 40) but on the Coppermills site (p. 47). Based on the arguments provided the solution appears appropriate but there is no information, e.g. results from trials, whole life costs comparison etc., to support the decision. The company states that there is no overlap with the WRMP as the algal bloom 'does not necessarily correlate with a dry year annual average planning scenario' (footnote p. 7). It is thus taken that the purpose of the treatment is to reduce the levels of algae down to acceptable levels during peak periods rather than install a system for continual operation, however continual operation may be beneficial. The company has not made clear whether there is any impact on site deployable output or process losses as a result of this intervention that may be a cost beneficial option to reduce supply-demand deficits. The company has not presented an evaluation of any potential synergies with long-term plans to support population growth although they do expect significant growth in these areas - albeit this is expected to be mitigated by demand management measures - thus they consider that there is a limited supply-demand programme with which to interact with. The company does not consider it feasible that the gateway desalination plant could be used to mitigate these risks. High Lift Pumping Station. The company proposes to commission an additional PS with connections to the strategic network and to retain the existing PS (albeit with modifications to the manifold) to remove this single point of failure (p. 4). Again, based on the argument provided the solution appears appropriate but there is no detailed information, e.g. CBA model, to support the decision. The scheme will be planned in AMP7 and delivered in AMP8 to ensure the new asset is configured correctly in light of the planned new works. The company may reconsider this part of their submission for final determination as the need for the new water treatment work to mitigate the loss of the entire site has not been accepted. A fuller description on anticipated network reinforcement would be required for a final determination. Power resilience (£23.4m) The company provides limited evidence regarding the alternatives considered. Thames Water describes the alternative solutions it considered in insufficient detail, for example "mobile and fixed generators are considered but the latter option is selected given that mobile generators are not always possible to install due to space or accessibility constraints" which indicates that options were not considered on a site-by-site basis. Additionally, although the company states that the most cost beneficial solutions have been chosen there is no evidence presented to allow assessment of this. Other alternatives are briefly mentioned (e.g. large batteries), but not discussed, and discarded as “not cost-effective” (although no further evidence is provided to demonstrate this). As a consequence, a 20% optioneering challenge is applied to this investment, passing £18.72m. The total investment passed within the gate is £81.220m | TW-CE_A7. Delivering long-term system resilience for London's water supply. TW-CE-A12 Resilience (excluding North East London water supply system). | Best option for customers | Fail | The company presents a range of options of addressing the issues for North-East London Resilience Scheme. The assessment of benefits are derived from the probability of the event and the number of customers expected to incur an interruption to supply and the customer valuation of such interruptions. The company has developed integrated solutions considering both risks identified however the WRMP strategy is not mentioned. In order to address the risk of algal blooms Thames Water proposes pre-treatment with a Mecana pile cloth filter (£50m) to restore Coppermills WTW to full output (1. s3.95). However Table 11 (1. pg 32) shows that this will not address the supply deficit although it addresses the risk - which requires clarification. Further, this option seems to be discounted as it does not address ‘the high level of dependency of the North East on Coppermills’, although it would address the risk highlighted and it is not clear what residual risk would not be addressed. The company further considers building a new WTW that draws from the Lee Valley reservoirs currently supplying Coppermills WTW. Although not mentioned by the company it is assumed that the works’ output can be maintained during algal blooms. The new works output is given as 45ML/d. This would therefore only marginally mitigate the reduced output from Coppermills WTW (taken to be 150ML/d). The zone would still be dependent on Coppermill, at least in the short term. Table 10 (pg. 31) shows a plan up to the end of AMP10 (2040) at a cost of £517m. Further Table 11 (pg 32) shows that Thames Water considers only the option of both pre-treatment at Coppermills and the new treatment work will addresses the estimated supply deficit and this is their preferred option (s3.110) to deal with the water quality issue. Thames Water propose replacing the HLPS at a cost of £56m of capex. However, they consider that there will remain a residual risk of failure of 1 in 150 years. This appears to be significantly over stated as it is not clear why they are not proposing to duplicate the HLPS, but to only replace it with a marginally better one. The company states that the current HLPS cannot be taken out of service so a duplicate would be needed to be constructed in any event and it would be logical to retain the asset going forward. The company consider that the replacement option does not address the fundamental issue only reduces its likelihood – hence they conclude that more supply capacity is needed. The company’s preferred option is to replace the HLPS and construct 300ML/d of extra WTW capacity over four AMPs (1. 3.119). Thames Water also proposes to construct the pre-treatment stage at Coppermills WTW although the rationale for this is unclear (1. s3.120). It is understood the company is still developing the details of this scheme. The power resilience solutions are generally for the provision of new, fixed and permanent standby generators, with an automatic start capability. Various flood resilience options are reported to have been reviewed and adopted measures are reported to include for raising of electrical equipment and local site bunds. The company state that the scope decisions and costs have been informed by similar works undertaken in AMP5 and AMP6. The works at the 25 sites are reported to provide "resilience improvements for 222 Ml/d of our water supply". Other than this limited evidence of alternative power or flooding options assessment provided. | as above
Robustness and efficiency of costs | Fail | The company has raised no substantive issues in its representation regarding the power resilience investment and we apply the company specific efficiency challenge as in draft determination (revised from 9% to 6%, see our ‘Company efficiency factor’ feeder model for more details). As a result, we allow £17.554m within this gate for the power resilience investment. For our decision regarding the London Water Supply resilience scheme see ‘PR19 final determinations: Thames Water – cost efficiency additional information appendix’. | TW-DD-001-Thames Water Response to Ofwat’s PR19 Draft Determination TW-DD-A04 - NEL supply resilience enhancement case | Robustness and efficiency of costs | Fail | The total expenditure assessed within the robustness and efficiency of cost gate is £81.220m which is comprised of the following: London Resilience Scheme (£62.5m). The company does not present a breakdown of costs. The company states that 'final output of cost assurance work is not available at time of writing' (p. 8). The costs include optimism bias which for the new WTW option vary from 22% to 44% (p. 56). For final determination it should be clarified the level and justification of optimism bias as applied to the allowed scope of work. On the basis that costs are not fully defined, the company specific efficiency challenge is applied, passing £56.70m. Power resilience (£18.72m). The company provides limited evidence regarding cost benchmarking or costs breakdown to demonstrate the robustness and efficiency of the cost estimates. Thames Water advises that a 14% efficiency challenge is applied to this investment as a result of forecast efficiencies in procurement and delivery. However, there is no evidence to assess the company's efficiency pre- or post- this challenge and that this specific investment is efficient. The company specific efficiency challenge is therefore applied, passing £16.99m. The total investment passed within the gate is £73.69m | TW-CE_A7. Delivering long-term system resilience for London's water supply. TW-CE-A12 Resilience (excluding North East London water supply system). Query TMS-DD-CA-004, May 2019 | Robustness and efficiency of costs | Partial pass | The company do not present a breakdown of their cost estimates. They state that the capital costs in their plan are ‘… adjusted to ensure we stay at the industry average position’ (1. s5.6). Therefore it would be appropriate to apply a further challenge to bring costs to efficient levels. Thames Water state that the power schemes were priced using its Engineering Estimating System (EES) and flood resilience schemes priced 'using expert judgement'. However, no further evidence / breakdown to support costs is provided except for statements that costs have been assured. Due to this lack of evidence cost have been adjusted. | as above
Customer protection | Pass | The company has raised no substantive issues in its representation regarding the power resilience and we retain our draft determinations assessment. For our decision regarding the London Water Supply resilience scheme see ‘PR19 final determinations: Thames Water – cost efficiency additional information appendix’. | TW-DD-001-Thames Water Response to Ofwat’s PR19 Draft Determination TW-DD-A04 - NEL supply resilience enhancement case | Customer protection | Pass | The need for customer protection against non-delivery has been assessed for the allowances made: London Resilience Scheme. As the final scope for delivery is uncertain the company proposes a gated process with joint working that will make a final decision used to adjust revenue limits. However, the allowed investment is relatively certain in scope and costs considered at an appropriate level. An on-going gated process is considered a disproportionate safeguard for customers for this value of programme allowed in AMP7 and protection could be adequately provided through a performance commitment. Performance commitment PR19TMS_BW12 has been designed to protect customer in the event of a delay or non-delivery of these schemes. Power Resilience. Thames Water proposes customer protection for this investment which is combined with its proposed investment in wastewater power resilience. We make allowances for both investments which are for the delivery of 47 schemes in total. However the company proposes a performance commitment with underperformance payments for delivery of fewer than 42 sites and outperformance payments for delivery of the remaining 5. In line with our approach to resilience, we consider that, given the low probability events that the scheme is mitigating against are unlikely to occur in the 2020-25 period, outperformance payments are not appropriate. We are intervening to set the performance commitment level to 47 by 2024-25, to reflect the enhancement cost allowance we have approved. As a result, we will remove outperformance payments for delivery of this investment and to strengthen customer protections we will amend the underperformance rate to return 50% of allowed funding to customers for non-delivery of schemes by 2024-25. |  | Customer protection | Partial pass | The company are proposing a financial ODI to cover the London resilience scheme with an underperformance payment the event of failure to meet the milestones on the project (CSD006-WNP-04b-Resilience, p44.) However the PC definition requires development as they state that the project scope is still being defined.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A
Further analysis / arguments
The HLPS is a critical asset and it is appropriate to address this single point of failure. A duplicated asset in a duty stand-by arrangement would address this at a cost of £56m. Accepting that the raw water is deteriorating and that this loss of deployable output is not double-counted in other supply-demand schemes providing pre-treatment at Coppermills is the least cost option at £50m to address this risk restore the works capacity. These issues have been taken in isolation as the overall strategy of TMS is unclear and they have not been clear on which residual risks they are seeking to reduce by increasing supply capacity by 300 ML/d in addition to these works. As both of these items are additional assets to enhance the sites no allocation of expenditure to base is considered appropriate. Considering the company have only benchmarked against average cost a further efficient challenge to the allowance of £106m would be appropriate at this stage.
Due to the lack of detail around the other resilience schemes costs have been reduced by 20% and subject to a company specific efficiency challenge

## Deep dive WSX
FD - Deep dive sheet - Wessex Water |  |  |  | DD - Deep dive sheet - Wessex Water |  |  |  | IAP - Deep dive sheet - Wessex Water
Summary at FD |  |  |  | Summary at DD
Company | WSX |  |  | Company | WSX
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 5.8067 |  |  | Totex carried through deep dive AMP7 (£m) | 5.8067
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 5.8067 |  |  | Totex assessed within deep dive (£m) | 5.8067 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 0.916 |  |  | Totex allowance from deep dive (£m) | 0.69616 |  |  | Expenditure carried through deep dive AMP7 (£m) | 38.427
Ofwat view of totex allowance for AMP7 (£m) | 0.916 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 0.69616 |  |  | Ofwat view of allowance for AMP7 (£m) | 5.31
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | The company has reallocated its ‘Partnership working’ scheme to improve SSSI sites (£0.528m) to a freeform line and it is assessed separately in the water freeform feeder model. The company has partially accepted our draft determination decision to consider MCCs (motor control centres) and gas store improvements as maintenance activities. However, the company has made representations in relation to [resilience improvements at a treatment works. Some information has been redacted.] We consider that these additional elements of the investment involve activities that are already funded as capital maintenance (e.g. replacement of switchboards and PLC equipment) and therefore we maintain our draft determination decision to pass the investment within the original scope of work (£0.916m). • PLC replacement (reduced to £1.890m from the original £2.400m): The company explains that “the PLCs are now a legacy product and will become obsolete within the next 5 years.” We consider this a capital maintenance activity that should be funded by base costs and therefore reject the investment in full. This is consistent with the information provided in the company’s original resilience submission, which states: “It has been assumed that the PLC replacement is capital maintenance so not included in any analysis”. [Information redacted.] The total value of the investment accepted within the need gate for final determinations is £0.916m. | 02 WSX DD Response - summary of our representations Representation C15 Resilience [Reference redacted] | Need for investment | Partial pass | The company has accepted the reallocations proposed during the IAP, including operational technological improvements linked to the end of PSTN lines (£11.3m), which has been moved from line 14 (Resilience) to 16 (Non SEMD Security). The company has reallocated a new investment (£0.528m) to resilience, stating: "Capex related to Partnership Working to improve SSSI landholdings in the Water Resources price control has been moved from line 13 (Investment to Address Raw Water Deterioration) to line 14 (Resilience). This reallocation is on a similar basis to WWS2a where Partnership Working was reassigned to Resilience as requested by Ofwat in the capex reallocations." The scheme is not well defined in terms of the resilience risk that the investment mitigates against, particularly because there is insufficient evidence of: the service failure mode and the probability of failure; how mitigating against the failure is currently beyond management control; the impact on customer service and; how the consequence of failure is beyond management control. However, we suggest that in its resubmission of the business plan tables for final determinations the company reallocates this investment back to the raw water deterioration line as we consider that the scheme involves activities (maintenance and catchment management activities) which are better assessed under this enhancement area. [Information redacted] The total investment passed within the need for investment gate is £0.916m. | Appendix 2 - Commentary on data tables that have changed 04.01 - Providing resilient services [Reference redacted] Query WSX-DD-CA-001, April 2019 | Need for investment | Partial pass | Resilience expenditure is expected to be related to low probability-high consequence events that would not be considered are part of routine operations. This investment relates to resilience improvements at [a treatment works] (£5.3m) and operational technology improvements. [Information redacted] Operational technology improvements are "...measures to counteract the increasing threat of malicious damage by third parties" and cessation of 3rd party communications services. Wessex Water links the need for the work to the end of PSTN telephone lines by 2025. The evidence of need provided appears robust, however, given the description it should be assessed as non-SEMD security related expenditure. | 04.01 - Providing resilient services, page 28-34 and 35.
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A | NA
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A | NA
Best option for customers | Pass | In its representation the company provides additional evidence of considering options and comparing them in terms of costs and benefits. As a consequence, we consider that an optioneering challenge is no longer needed for the accepted investments. The total value of the investment accepted within the gate for final determinations is £0.916m. | 02 WSX DD Response - summary of our representations Representation C15 Resilience [Reference redacted] | Best option for customers | Fail | The total expenditure assessed within the options gate is £0.916m. [Information redacted] For draft determinations, we have revised the evidence provided by the company applying the refined assessment criteria developed following the IAP and companies’ responses. The company states that it has carried out a CBA as part of its optioneering process although there is insufficient evidence of this. Further, the company states: "The CBA analysis work is currently ongoing but would suggest that the resilience improvements to [Information redacted] to improve on-site redundancy and reliability are cost beneficial". A 20% efficiency challenge is therefore applied to the accepted investments. The total investment passed within the gate is £0.733m. | [Reference redacted] [Reference redacted] | Best option for customers | Partial pass | Wessex Water describes undertaking a cost / benefit analysis (CBA) to assess the appropriate investment level/option to improve the resilience of the works. The analysis aimed to compare the value the reduction in outage risk (additional costs associated with "managing any incident, customer costs, reputation costs, external stakeholder costs and any penalties and fines imposed") against the cost of investing to improve the resilience. | [Reference redacted]
Robustness and efficiency of costs | Pass | In its representation the company provides a cost breakdown of activities and for this reason we consider that the specific cost efficiency challenge is no longer needed for the accepted schemes. The total value of the investment accepted within the gate for final determinations is £0.916m. | 02 WSX DD Response - summary of our representations Representation C15 Resilience [Reference redacted] | Robustness and efficiency of costs | Fail | The total expenditure assessed within the robustness and efficiency of cost gate is £0.733m. The company provides estimates of the costs for each general investment area. While the company states that external benchmarking has been used and presents generic comparisons of construction and non-construction costs against benchmarks, there is insufficient evidence to demonstrate the efficiency and robustness of the costs estimated for the resilience programme. For example, the company states that “our approach was to ask each cost consultant to estimate the construction costs for a selection of projects” (…) “our aim was to have over 50% of the enhancement programme benchmarked”. (8.11, p.10); however, the company omits the detail of the benchmarked projects and whether any of these relate to the resilience programme. As a consequence, a cost efficiency challenge has been applied to the accepted schemes. The total investment passed within the gate is £0.696m. | 08.11 - Assessing the costs of our enhancement programme (September 2018) | Robustness and efficiency of costs | Partial pass | The company states that external benchmarking has been used to demonstrate that its "cost estimates are efficient and competitive compared with the marketplace". The costs of the mitigation interventions were costed using internal and external sources. The lack of cost breakdown means that a refined approach to cost reallocation has not been feasible. A company specific efficiency factors has been applied. | 04.01 - Providing resilient services, page 28-34
Customer protection | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | 02 WSX DD Response - summary of our representations Representation C15 Resilience [Reference redacted] | Customer protection | Pass | The need for customer protection against non-delivery has been assessed for the allowed schemes. The materiality of the allowed investment is small in comparison to the company's proposed totex within the water network plus and water resources price controls and so customer protection against non-delivery is not imposed. |  | Customer protection | Pass | The company includes the range of common resilience and asset health PCs designed to incentivise resilience. The company has not proposed a specific PC associated with the delivery of the resilience enhancements, given the scale and nature of the schemes this is considered appropriate.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A | NA
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A | NA

## Deep dive AFW
FD - Deep dive sheet - Affinity Water |  |  |  | DD - Deep dive sheet - Affinity Water |  |  |  | IAP - Deep dive sheet - Affinity Water
Summary at FD |  |  |  | Summary at DD
Company | AFW |  |  | Company | AFW
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 15.466 |  |  | Totex carried through deep dive AMP7 (£m) | 15.466
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 15.466 |  |  | Totex assessed within deep dive (£m) | 15.466 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 13.566 |  |  | Totex allowance from deep dive (£m) | 13.566 |  |  | Expenditure carried through deep dive AMP7 (£m) | 5.3
Ofwat view of totex allowance for AMP7 (£m) | 13.566 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 13.566 |  |  | Ofwat view of allowance for AMP7 (£m) | 3.3
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | Affinity Water has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. We pass £13.866m through the gate. | AFW-CE | Need for investment | Partial pass | The total expenditure assessed within the resilience water enhancement line is £15.466m (all Capex) and comprises of the following: - Horsley Cross water treatment works enhancement £3.100m - £1.500m is passed, the remaining expenditure is considered base cost. A review of the evidence provided by the company in September 2018 business plan and provision of new evidence at draft determination has confirmed the ‘Horsley Cross WTWs enhancement’ scheme was submitted under the water resilience enhancement line. No allowance is made for the ‘Single point of failure’ scheme as this was submitted by the company as base expenditure not enhancement expenditure. The company has identified that Horsley Cross WTW's presents a single point of failure risk for 72,000 customers in the Brett community. Affinity Water response to Query AFW-DD-CE-005 demonstrates that supply to 72,000 customers would be cut off for an extended duration in the event of a key asset failure. Duplication of the raw water intake is accepted as the risk is considered high consequence - low probability and beyond company control. Repair of deeply buried large diameter mains would take in excess of 72 hours with reservoir storage only providing buffer for 24 hours duration. Motor control centre (MCC) replacement to split the power supply and upgrading the power supply onsite generation to increase redundancy is considered a renewal cost which is part of the base allowance (Refer AFW-DD-CE-005). - Supply 2040 schemes (ST9, ST10, ST13 and ST14) £12.366m - passed. This expenditure has been reallocated from Supply Demand Balance as the water supply deficit does not justify investment until beyond AMP7 (Refer Supply 2040 Revised Draft WRMP). Booster pump stations (Preston to Sundon and Bulls Green to Preston) and cell storages (Chual End and Preston) mitigate against the risk of a 48 hour loss of Grafham water treatment works (Severn Trent Asset) or strategic mains failure. 24,000 properties will be supplied by Grafham WTWs on a daily average and up to 122,000 properties during peak dry conditions at the end of AMP 7. Affinity Water states it has insufficient headroom in groundwater sources and insufficient storage to meet customer demand in the event of an outage of Grafham WTWs. As Grafham WTWs is a third party asset and beyond company control to manage, this investment is supported to protect against a long interruption. The Resilience and environmental pilot has been withdrawn from the April 2019 business plan, it was previously submitted in the September 2018 business plan, therefore this scheme has not been assessed at draft determination. The total investment passed within the need for investment gate is £13.866m. | Securing Cost Efficiency Appendices March 2019, pg 31-39 Technical Report 4.14: Supply 2040 Revised Draft Water Resource Management Plan 2020-2080, pg 27-32 Query AFW-DD-CE-005, May 2019 Our Business Plan for 2020 – 2025 Appendix 9 – Ensuring Long-Term Resilience September 2018, pg 51 | Need for investment | Partial pass | The company has provided a suitable needs case for resilience spend related to Single Point of Failure (SPoF) issues that are linked to low likelihood high impact events and therefore do fall under resilience spend. The company states that "A Single Point of Failure (SPoF) is defined as an asset failure leading to loss production/availability where the residual output is insufficient to meet normal requirements. The state that “the designed resilience of our systems ensures that the two components (asset failure subsequent loss of supply) are infrequent. However, a few, low likelihood, high consequence risks associated with asset failure which could lead to significant loss of supply remain. Typical examples include severe fire affecting electrical infrastructure at large treatment works, failure of trunk mains, asset failures at sites where customer supplies are almost immediately affected and sudden inundation of infrastructure assets within basements." (Appendix 9, p50) An additional £2m was assessed under line 14 that was reallocated from line 8 SDB for resilience and environment community pilot schemes. The expenditure for this would be expected as part of base spend (Appendix 6, 8.5.6.2, p288). | Appendix 9, p50 Appendix 6, p288
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A | NA
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A | NA
Best option for customers | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. We note however that the gate was incorrectly shown as pass and has been corrected to partial pass as we apply an options efficiency challenge to part of the proposed investment. We pass £13.566m through the gate. | AFW-CE | Best option for customers | Pass | The total expenditure assessed within the options gate is £13.866m which is comprised of the following: - Horsley Cross WTW enhancement £1.500m - Fail - 20% options efficiency challenge is applied, £1.200m is passed. Options have been considered within the broader risk and resilience methodology and have been filtered down to those that represent best value for customers, best whole of life cost etc. There is indication that customers were consulted during this process and that prevention of critical asset failure is broadly supported by customers to provide uninterrupted supply, however there is limited evidence to demonstrate that this specific scheme has customer support or the best option has been selected. There is limited to no evidence of options investigation or cost benefit analysis (Reference Appendix 9 - Ensuring Long-Term Resilience p.g. 51) - Supply 2040 schemes (ST9, ST10, ST13 and ST14) £12.366m - Pass - A range of options have been investigated for each piece of investment, with the preferred solutions having the lowest cost and highest resilience score based on bespoke resilience benefit scoring methodology. Costs for the scheme have been reduced by approximately 37% (compared to the September 2018 business plan) for these four schemes (£19.620m to £12.366m) which is well below the overall efficiency challenge applied (approximately 26%) at initial assessment of plan (IAP) stage within supply demand balance (Refer Securing Cost Efficiency Appendices March 2019; Supply 2040 Revised Draft WRMP). | Technical Report 4.14: Supply 2040 Revised Draft Water Resource Management Plan 2020-2080, pg 30 Securing Cost Efficiency Appendices March 2019, pg 7, 31-39 Our Business Plan for 2020 – 2025 Appendix 9 – Ensuring Long-Term Resilience September 2018, pg 46, 51 Query AFW-DD-CE-005, pg 3-4 | Best option for customers | Partial pass | The company has stated that it has conducted optioneering as part of its resilience methodology to identify the best value option for customer (Appendix 9, s1.4, p9). However, how the process was conducted, i.e. what alternative options were considered or the cost benefits of the preferred and alternative options could have been better evidenced. The company has presented very limited evidence of customer engagement on resilience issues. It is not apparent to us that the company has engaged with customers in any depth to inform its resilience strategy. The company has presented limited evidence of consideration of alternative options. However, the company's plan does suggest it has taken on the 4Rs approach to developing resilience and associated schemes. "We have used extensively the Cabinet Office 4Rs model (Resistance, Reliability, Redundancy and Response & Recovery) in our previous plan. For the development of our 2020-2025 plan, we have considered short, medium and long-term resilience in a round." (Appendix 9, s1, p4) | Appendix 9, s1.4, p9 p152 of V4BP
Robustness and efficiency of costs | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. We pass £13.566m through the gate. | AFW-CE | Robustness and efficiency of costs | Pass | The total expenditure assessed within the robustness and efficiency of cost gate is £13.566m which is comprised of the following: - Horsley Cross WTW enhancement £1.200m - pass - No further evidence is provided to support the cost efficiency of this scheme, however a 6.1% cost reduction has been made which matches the company efficiency challenge applied during IAP. - Supply 2040 schemes (ST9, ST10, ST13 and ST14) £12.366 - pass - No further evidence is provided to support the cost efficiency of this scheme however (as stated in in the best option for customers gate above), the scheme cost is below the efficiency challenge set at IAP. The company has explained its costing methods using its own cost models or bottom up cost estimates, benchmarked framework costs, optimisation and had costs independently audited and benchmarked. | Our Business Plan for 2020 – 2025 Appendix 6: Wholesale Technical Support Document September 2018, pg 195-264 | Robustness and efficiency of costs | Fail | For the SPoF schemes the company have also stated that they have taken a proportionate approach to schemes to keep them affordable and utilise existing measures to mitigate risks (Appendix 9, p50). However this is not backed up by further evidence showing what the different alternatives to the overall plan were and why this combination of schemes is considered the most efficient. | Appendix 9, s1, p4 Appendix 9, p50
Customer protection | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | AFW-CE | Customer protection | Pass | Pass - Affinity Water has a proposed a bespoke performance commitment to protect against high consequence low probability risks including unplanned interruptions to supply >12 hrs which covers these schemes from a resilience perspective (Reference Securing Long Term Resilience Evidence Document March 2019, p.g. 4) | AFW Securing Long Term Resilience Evidence Document March 2019, pg 4 | Customer protection | Pass | The company includes the range of common resilience and asset health PCs designed to incentivise resilience. The company has not proposed a specific PC associated with the delivery of the resilience enhancements, given the scale and nature of the schemes this is considered appropriate.
Affordability | N/A |  |  | Affordability | N/A | - |  | Affordability | N/A | NA
Board assurance | N/A |  |  | Board assurance | N/A | - |  | Board assurance | N/A | NA
Further analysis / arguments
Scheme Requested Allowed
Community Resilience Pilots £2m £0m
SPoF schemes £3.3m £3.1m

## Deep dive BRL
FD - Deep dive sheet - Bristol Water |  |  |  | DD - Deep dive sheet - Bristol Water |  |  |  | IAP - Deep dive sheet - Bristol Water
Summary at FD |  |  |  | Summary at DD
Company | BRL |  |  | Company | BRL
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 11.96 |  |  | Totex carried through deep dive AMP7 (£m) | 11.96
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 11.96 |  |  | Totex assessed within deep dive (£m) | 11.96 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 8.1 |  |  | Totex allowance from deep dive (£m) | 5.6672 |  |  | Expenditure carried through deep dive AMP7 (£m) | 0
Ofwat view of totex allowance for AMP7 (£m) | 8.1 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 5.6672 |  |  | Ofwat view of allowance for AMP7 (£m) | 0
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | Bristol water does not raise substantive issues on our assessment within the need gate of the ‘Glastonbury-Street’ component of its ‘critical mains – populations at risk’ investment, £7.084m). It makes representations on our draft determination allowances regarding the remaining components of the ‘critical mains - populations at risk’ investment (£4.063m) and the ‘critical mains exceptional sites’ investment (£0.815m). - Critical mains populations at risk (31.003.04) £11.147m – We retain our draft determination decision regarding the Glastonbury-Street’ component of this investment (£7.084m). The remaining component of the investment is for 36 mains which are considered ‘single points of failure’ (£4.063m). For final determinations the company provides additional evidence to demonstrate the need for this investment. There is sufficient evidence that a portion of the investment mitigates against low probability failures that would result in high consequence supply interruptions for customers, for example the failure of the Chase outlet main would result in an interruption in excess of 24 hours. However, beyond the limited examples provided, the company specifies that the failures would result in a supply interruption of between 30 minutes and 24 hours. Additionally, the factors outside of management control are not set out for each investment. Consequently, the evidence for the majority of the investment is insufficient to demonstrate that each failure is beyond management control and would result in high consequences for customers. We consider that some of the failures with unspecified duration of interruptions would have high consequences to customers. To determine an appropriate allowance for the investment we consider the evidence of historical supply interruption events on these mains and determine that 25 percent of failures resulted in a supply interruption of more than 24 hours (ie high consequence to customers). We pass £1.016m through the needs gate which accounts for 25% of the investment in line with our assessment of the portion of the investment we consider to be high consequence. - Critical mains exceptional sites (01.002.05) £0.815m, Bristol Water provides further evidence to support the need for this investment but we do not make an allowance. Bristol Water clarifies in its representation that the investment is for remedial measures at 6 exceptional sites and that investigations and testing is not included as part of the cost. The evidence provided that the investment will mitigate specific identified risks on trunk mains is not sufficient and convincing. The investment is based on broad assumptions and approximations and is insufficiently scoped. Consequently, we do not revise our draft determination allowance for this investment. The total investment we pass within the gate is £8.100m, which includes the additional £1.016m which we now pass at final determination. | BW02-8 Detailed Resilience Investment Case Evidence and Appendices | Need for investment | Partial pass | The total expenditure assessed within the resilience water enhancement line is £11.960m (all Capex) and comprises of the following: - Critical mains (Populations at risk) (31.003.04) £11.147m - Partial pass. This investment is proposed to mitigate risk relating to interruption of supply in population centres over 10,000 people, caused by critical asset failure. £7.084m is passed for the Wells to Glastonbury - Street area main, for a new 8km main providing a secondary source of supply to 28,000 customers in the Glastonbury – Street area. This investment mitigates against the low likelihood high consequence risk of an extended duration supply interruption. The existing supply main is located within flood prone land (Environmental Agency flood zone 3), if the main failed during a period of prolonged flooding, access and repair of the main would not be possible (Refer BRL-DD-CE-008); £4.061m is failed, addressing 36 ‘Single points of failure’ in the network is considered base expenditure. The scheme is for the installation of short lengths of mains, dynamic valves, manual valves and turbidity meters. Some evidence is provided to demonstrate that critical mains failure is low likelihood, however there is limited evidence provided to demonstrate that the majority of ‘significant’ incidents are a result of extended isolations (>24 hours) due to extenuating circumstances. The scheme includes mitigations for single source of supply mains where a 24 hours loss of service results in supply interruption or low pressure events > 30 minutes. There is insufficient evidence that this risk is high consequence with the duration of interruption or low pressure only 30 minutes or more. The investment is considered to be benefiting supply interruptions and water quality targets more so than mitigating against high consequence – low likelihood events. In addition there is inconsistency in the prioritisation method for interventions in AMP7 and AMP8 with a number of interventions benefiting a lower number of customers put ahead of those benefiting a greater numbers of customers. - Critical mains (Exceptional sites) (01.002.05) - £0.815m - Failed. Mitigating the risk at six exceptional sites on trunk mains that are low likelihood of failure and would be difficult to repair and restore. This scheme is to undertake investigative work (testing and inspection) which is considered to be a base activity. This is part of the Trunk Mains and Pipe Bridges Investment Case. The following three schemes: Whitchurch to Stowey 21 inch diameter main improvements (31.001.01); Forum to Millmarsh 10 inch diameter main replacement (31.001.02); and System Resilience Assessments (31.003.03) are part of base expenditure. The total investment passed within the need for investment gate is £7.084m | C5C Technical Annex 2 Resilience Enhancement Investment New, April 2019 Query BRL-DD-CE-008 C5B Technical Annex 02 Trunk Mains and Pipe Bridges Investment Case: Technical Approach and Business Case NTPBP-INV-TRU-0526 September 2019, pg 35 | Need for investment | Fail | The company has not provided sufficient evidence that the investment presented relates to enhancement resilience line. Resilience expenditure is expected to be related to low probability-high consequence events that would not be considered as part of routine operations. We consider that the investment sought relates to repairing or refurbishing mains which have known issues (£1.56m) and that for conducting risk assessments (£0.29) should be covered under base. The investment to reduce the impact of supply interruptions from critical assets (£10.25m) proposes investments to ensure that issues lasting more than 24hrs with one of our critical assets do not impact more than 10,000 people by 2030. The analysis looks at failures lasting for 24hrs or more but doesn’t present evidence or analysis on the likelihood of the failures lasting 24hrs and further the company in fact states that this has not been robustly analysed. The company does not clearly identify the types of failures the risk analysis has considered, and whether these only consider low probability-high consequence events and not risks that are not already managed within existing operational responses. The company should provide further evidence to justify that the failure lengths considered are appropriate and what failures have been assessed to justify the need. | BRL.C5B.TA17, 4.2, p23-36
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A
Best option for customers | Pass | We assess £8.100m in the options gate for the critical mains (populations at risk: 31.003.04) investment as follows: - The Wells to Glastonbury-Street main investment £7.084m. Bristol Water provides new evidence in its representation in response to our options efficiency challenge that was applied at draft determination. The evidence is sufficient and convincing to demonstrate that alternative options have been considered by the company. The alternative options are discounted on the basis of being more expensive or not sufficiently mitigating the risk of supply interruption. For final determination we do not apply an options efficiency challenge. - The critical mains ‘single points of failure’ investment of £1.016m passes our assessment. Bristol Water states that a range of resilience options are considered for the investments at a high level including duplications, valve installation and turbidity meters and selection of lowest cost option (valving) being preferred over other more expensive options. We consider the materiality of this investment and determine that the company demonstrates that it has selected low cost solutions. We do not apply an optioneering challenge. The total investment we pass within the gate is £8.100m. | BW02-8 Detailed Resilience Investment Case Evidence and Appendices | Best option for customers | Fail | The total expenditure assessed within the options gate is £7.084m which is comprised of the following: - Critical mains (Populations at risk) - Glastonbury Street Area main - £7.084m - Fail - 20% options efficiency challenge is applied - £5.667m is passed. A range of resilience options have been considered for the schemes at a high level including duplications, valve installation and turbidity meters and selection of lowest cost option (valving) being preferred over other more expensive options. There is very limited optioneering evidence for the Glastonbury - Street main investment. Bristol Water states that it has selected ‘the most expensive mitigation option available... considered when none of the other mitigation options detailed above were viable’. There is some evidence to demonstrate that it has completed optimisation and cost/benefit analysis, however for a scheme of this cost it would be expected that options and cost/benefit analysis would consider route selection/ pipeline cost optimisation etc. Furthermore, the secondary source of supply is proposed to have a larger diameter than the existing main (18 inch compared to 15 inch diameter), the additional capacity is not justified (Reference C5C Technical Annex 2 Resilience Enhancement Investment New p.g. 8-9; BRL.C5B.TA17 Resilience Investment Case, pg 20, pg 28-35, Appendix E) The company states that customers had mixed views regarding interruptions and major water supply events, preferring lower cost options. Customers showed 75% support for these service areas during final plan testing and 65% willingness to pay. The total investment passed within the gate is £5.667m | C5C Technical Annex 2 Resilience Enhancement Investment New, April 2019, p.g. 8-9 BRL.C5B.TA17 Resilience Investment Case September 2018, pg 20, pg 28-35, Appendix E | Best option for customers | N/A
Robustness and efficiency of costs | Pass | We assess £8.100m in the robustness and efficiency of cost gate for the critical mains (populations at risk: 31.003.04) investment as follows: - Wells to Glastonbury Street main £7.084. Cost estimation is based on a consultant and company unit cost model for pipelines. We consider the costs are efficient in relation to other comparable investments of a similar type and scale, so we do not apply the company specific efficiency challenge. - Critical mains populations at risk ‘single points of failure’ investment of £1.016m. Cost estimation is based on consultant and company unit cost models for valving and pipework. The unit cost models provided and the allocation of costs for each investment are reasonable for these small scale investments and so we do not apply the company specific efficiency challenge. The total investment allowance is £8.100m, which includes an additional £1.016m which we now pass at final determination. | BW02-8 Detailed Resilience Investment Case Evidence and Appendices | Robustness and efficiency of costs | Pass | The total expenditure assessed within the robustness and efficiency of cost gate is £5.667m which is comprised of the following: - Critical mains (Populations at risk) - Glastonbury Street area main £5.667m - Pass - Capex costs for each individual mitigation intervention were costed based on unit costs and uplifts provided by a consultant using industry comparable cost data. Data assurance has been undertaken. There is no evidence of benchmarking, assurance of costs or a cost breakdown for the scheme. However, it is evident that the scheme was costed at £7.700m and the company has applied a self-imposed 8% efficiency challenge to these costs, bringing the cost down to £7.084m. On this basis the efficiency of cost is passed. The total investment passed within the gate is £5.667m. | C5C Technical Annex 2 Resilience Enhancement Investment New, April 2019, pg. 10 BRL.C5B.TA17 Resilience Investment Case September 2018, p.g. 21 , p.g. 37 Appendix E | Robustness and efficiency of costs | N/A
Customer protection | Partial pass | The company raises concerns in its response to our draft determination regarding the suitability of the performance commitment that we introduced Glastonbury-Street Network Resilience and the change to the original performance commitment ‘Populations at risk from asset failure.’ We maintain our draft determination decision to protect customers against non-delivery of the Wells to Glastonbury-Street main. For further details refer to outcomes assessment. The remaining allowance for ‘Critical mains - populations at risk’ investment does not require customer protection due to the low materiality of the investment. | BW02-8 Detailed Resilience Investment Case Evidence and Appendices | Customer protection | Partial pass | Bristol Water proposes a bespoke performance commitment to protect customers in population centres >10,000 customers from supply interruption due to critical asset failure. Due to the disallowance of the ‘Single points of failure’ component of the Critical mains (Population at risk scheme), this is not considered suitable to protect customers. To protect customers from non-delivery we have proposed to introduce an underperformance only outcome delivery incentive to ensure delivery of the Wells to Glastonbury Street area main scheme with the target of 100% completion by the end of AMP7 (2024-25), this is further detailed in outcomes. | C5C Technical Annex 2 Resilience Enhancement Investment New, April 2019, pg. 6 | Customer protection | N/A
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A

## Deep dive HDD
FD - Deep dive sheet - Hafren Dyfrdwy |  |  |  | DD - Deep dive sheet - Hafren Dyfrdwy
Summary at FD |  |  |  | Summary at DD
Company | HDD |  |  | Company | HDD
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 1.65 |  |  | Totex carried through deep dive AMP7 (£m) | 1.65
Totex assessed within cost adjustment claims (£m) | 0.5 |  |  | Totex assessed within cost adjustment claims (£m) | 0.5
Totex assessed within deep dive (£m) | 1.15 |  |  | Totex assessed within deep dive (£m) | 1.15
Totex allowance from cost adjustment claims (£m) | 0.5 |  |  | Totex allowance from cost adjustment claims (£m) | 0.5
Totex allowance from deep dive (£m) | 0 |  |  | Totex allowance from deep dive (£m) | 0
Ofwat view of totex allowance for AMP7 (£m) | 0.5 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 0.5
Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | Hafren Dyfrdwy has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. We accept £0.500m, which is assessed as a cost adjustment claim | Chapter 4 Securing cost efficiency | Need for investment | Partial pass | The total expenditure assessed within the resilience water enhancement line is £1.650m (all Capex). £0.500m is part of the Reservoir Safety cost adjustment claim (CAC) and is accepted. The assessment of this CAC has been completed in the CAC Feeder Model. The remaining £1.150m is failed. There is no explanation for this expenditure. It appears that the expenditure has been incorrectly included for the CAC named ‘Supply Resilience’, which has been withdrawn by the Company in the April 2019 submission. The total investment accepted is £0.500m | Hafren Hyfrdwy 2020-2025 Business Plan, Revised Plan 1 April 2019, pg 105
Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A
Best option for customers | Not assessed | The company has not raised substantive issues in its representation and we retain our draft determination decision regarding this gate. | Chapter 4 Securing cost efficiency | Best option for customers | Not assessed
Robustness and efficiency of costs | Not assessed | The company has not raised substantive issues in its representation and we retain our draft determination decision regarding this gate. | Chapter 4 Securing cost efficiency | Robustness and efficiency of costs | Not assessed
Customer protection | Not assessed | The company has not raised substantive issues in its representation and we retain our draft determination decision regarding this gate. | Chapter 4 Securing cost efficiency | Customer protection | Not assessed
Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A

## Deep dive PRT
FD - Deep dive sheet - Portsmouth Water |  |  |  | DD - Deep dive sheet - Portsmouth Water |  |  |  | IAP - Deep dive sheet - Portsmouth Water
Summary at FD |  |  |  | Summary at DD
Company | PRT |  |  | Company | PRT
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 2.793 |  |  | Totex carried through deep dive AMP7 (£m) | 2.793
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 2.793 |  |  | Totex assessed within deep dive (£m) | 2.793 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 1.1701 |  |  | Totex allowance from deep dive (£m) | 1.1701 |  |  | Expenditure carried through deep dive AMP7 (£m) | 2.548
Ofwat view of totex allowance for AMP7 (£m) | 1.1701 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 1.1701 |  |  | Ofwat view of allowance for AMP7 (£m) | 2.548
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | Portsmouth Water submits representations on our draft determination regarding ‘resilience schemes,’ scheme 3 – supply deficit Farlington, claiming the same amount as in April 2019, that are assessed below. The total amount we assess within the needs gate is £2.793m (all capex). - For Scheme 3 - supply deficit Farlington (£1.304m): we maintain our decision not to pass this investment. Portsmouth Water provides further evidence to support this investment. The company states that the investment includes “a key transfer main from Hoads Hill (Quay Road), which was condition tested in AMP5 and found to be nearing the end of its predicted life.” As a result, we consider this investment is mostly funding the renewal of the Hoads Hill water main for which the company receives a base allowance and therefore it is not accepted as a resilience enhancement. Portsmouth Water also argues in its representation that Farlington water treatment works is the company’s largest and most strategic source and that there is a risk of oil contamination which could cause outage of the water treatment works and customer supply interruption because there will be a supply deficit as well as turbidity. However, we consider these risks within management control (e.g. catchment management and volatile organic compound monitoring). The company has not raised substantive issues in its representation regarding the following resilience schemes: scheme 1 oil pollution at water treatment work’s £0.369m; scheme 6A - Hoads Hill to Gosport main' £0.548m; and 7 Nelson to Waterlooville and Lovedean main £0.252m all of which we pass. As well as regarding ‘resilience studies’ £0.0749m and ‘Strategic mains support’ £0.245m both of which we do not pass. We pass £1.170m, which remains unchanged from our draft determination. | PR19 DRAFT DETERMINATION REPRESENTATION FINAL Appendix 3.2.1a Resilience Study Appendix 3.2.1b Quay Rd | Need for investment | Partial pass | The total expenditure assessed within the resilience water enhancement line is £2.793m (all capex) and comprises of the following: -Resilience schemes £2.472m, 3 out of 4 components of this investment are passed, totalling £1.170m. This reduction in allowance since IAP is based on the provision of more detailed information by the company at draft determination and the application of a refined acceptance criteria for resilience enhancement which is described in the model cover sheet. 'Scheme 1 - oil pollution at WTW's' (£0.369m) is passed. The investment is for mitigation against oil contamination from groundwater sites entering water treatment works and is for the installation of monitoring equipment to detect it and shutdown treatment works. 'Scheme 6A - Hoads Hill to Gosport main' (£0.548m) is passed, the investment mitigates against the failure of a critical crossing of a motorway, which if this section fails Gosport would be without water supply and the failure of this main ‘would be difficult to respond to and recover from quickly’. 'Scheme 7 - Nelson to Lovedean main' (£0.252m) is passed. The investment upgrades Leigh park booster to 8 Ml/d and 30m head to mitigates the loss of the 36” main from Nelson Reservoir to Waterlooville and Lovedean in combination with potential nitrate contamination at Lovedean water treatment works to which the treatment plant has been a historically susceptible asset. 'Scheme 3 - supply deficit Farlington' (£1.304m) is failed. The investment increases transfer capacity to the Farlington zone to mitigate against failure of the Farlington treatment works or another production site. It is evident that the solution is mostly funding renewal (the cost breakdown confirms this) of the Quay Road main, it is stated to have ‘a short remaining asset life’ which is considered base maintenance and therefore not enhancement expenditure. (Reference Query PRT-DD-CE-004; PPA_1102 - Resilience schemes Technical direction statement, June 2017 p.g. 14-20 ; S795.PPA.1102 Asset management position paper – Network and supply resilience schemes, p.g. 7). - Resilience studies £0.0749m, is failed. This investment relates to modelling and prioritisation of resilience schemes for AMP8 (Refer RP017 - Resilience Studies). We initially made an allowance for this scheme at IAP, however we do not make an allowance at draft determination because implicit allowances are made for investigations within base, therefore it is not considered to be enhancement. - Strategic mains support £0.245m is failed. This is growth related expenditure (Refer MS003_Network Resilience). At the IAP we reallocated investment driven by growth to the growth line for assessment alongside other similar investments. For Draft Determinations we have incorporated enhancement costs which are driven by growth in our base plus cost econometric models. Therefore, we do not make an additional allowance for it in this line or reallocate it for assessment elsewhere, since we assume it is included within our modelled base plus allowance. The total investment passed within the gate is £1.170m. | - AMP7_PPA_1102 - Resilience Schemes, April 2018 - Asset management planning Miser Criticality Modelling Technical Direction Statement, June 2017, p.g. 14-20 - Query PRT-DD-CE-004, May 2019 - 9.11.1 MS001 - Resilience VOC monitors - 9.10.5 T02_Farlington_Resilience - 9.11.3 MS007 - Resilience Nelson to Lovedean - 9.11.2 MS003 - Network Resilience - 9.11.6 RP017 - Resilience Studies -S795.PPA.1102 Asset management position paper – Network and supply resilience schemes, p.g. 7 | Need for investment | Partial pass | Three resilience programmes totalling £2.79m have been included within line 14 these include: 1) AMP7_PPA_1101 - Resilience Studies v2 30Jan2018 - £74.9k 2) AMP7_PPA_1102 - Resilience Schemes V5 30Apr18 - £2,472.7k 3) AMP7_PPA_1105 - Strategic Mains Support - £245.0k 1) 1101 - Resilience studies - The proposed studies follow on from similar modelling done in AMP7 which has identified potential points of failure and allowed prioritisation of schemes based on consequence and cost benefit analysis. The modelling has been used to identify the impacts and most cost beneficial schemes to mitigate against low probability high magnitude events within the AMP7 business plan and therefore the allowance is accepted for planning for AMP8, (9.11.6 RP017 - Resilience Studies, p2) (AMP7_WS2 Data Tables Commentary TH, p2). 2) 1102 - Resilience Schemes: Four major Resilience schemes are planned in AMP7, these are new schemes to off-set potential demand deficits arising from high risk low likelihood failure events. (AMP7_WS2 Data Tables Commentary TH, p2). The schemes identified here were as a result of MISER resilience modelling which assessed a range of failure scenarios. The need for the proposed schemes has been evidenced through a detailed modelling approach, the failure scenarios modelled largely cover low probability high magnitude events and therefore meet our expectation of resilience needs. (Resilience Study: Project Report, s3.1, p4-5) (Resilience Study: Project Report, s3.3.4, p8) (Resilience Study: Project Report, s3.4, p10). 3) 1105 - Strategic Mains Support: The £0.245m of investment related to upsizing or preparing the network for anticipated development is considered under the New Developments enhancement line as it relates to preparing for expected growth of new developments. | 9.11.6 RP017 - Resilience Studies AMP7_WS2 Data Tables Commentary TH Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit 9.5 WAP Appendix 5_Enhancement for Resilience in the Round, p8
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A
Best option for customers | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. We pass £1.170m within this gate. | PR19 DRAFT DETERMINATION REPRESENTATION FINAL Appendix 3.2.1a Resilience Study Appendix 3.2.1b Quay Rd | Best option for customers | Pass | The total expenditure assessed within the options gate is £1.170m which is comprised of the following: - Resilience schemes £1.170m (schemes 1, 6a and 7) , pass, the company presents sufficient evidence of the range of alternative options identified, analysing 880 failure scenarios and consideration of the most cost beneficial combination of interventions to identify best value for customers. Although alternatives for each of the selected investments are not identified, the benefit cost of the investments is high and there is evidence that optimisation/ value engineering was completed to select the optimal combination of schemes. (9.8.4.1_AMP7_SERVALEC MISER resilience modelling, Table 3, p12). 'Scheme 3' has not been assessed in this gate at draft determination as it has not passed the needs gate. The resilience programme has also been externally assured which verifies the approach and solutions proposed are suitable. (Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit, p3). Resilience studies has not been assessed in this gate at draft determination as it has not passed the needs gate. The total investment passed within the gate is £1.170m | 9.8.4.1_AMP7_SERVALEC MISER resilience modelling, Table 3, p12 Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit, p3 | Best option for customers | Pass | The company presented sufficient evidence of the range of alternative options identified and consideration of the most cost beneficial combination of interventions to identify best value for customers. (9.8.4.1_AMP7_SERVALEC MISER resilience modelling, Table 3, p12). The resilience programme has also been externally audited by Atkins who stated that the optioneering and scope development was "In line with industry good practice, based on screening and then reasonably detailed optioneering for the preferred AMP7 schemes." The external audit also challenged the probability of failure rates used but stated that "Although there is uncertainty over failure probabilities, and we challenged that validity of those calculations at audit, the four preferred options clearly have a very high benefit: cost ratio and remain justified even if more realistic failure probabilities are applied." (Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit, p3). Overall, the evidence provided was considered sufficient. | 9.5 WAP Appendix 5_Enhancement for Resilience in the Round, p8 9.8.4.1_AMP7_SERVALEC MISER resilience modelling Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit, p3
Robustness and efficiency of costs | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. We pass £1.170m within this gate. | PR19 DRAFT DETERMINATION REPRESENTATION FINAL Appendix 3.2.1a Resilience Study Appendix 3.2.1b Quay Rd | Robustness and efficiency of costs | Pass | The total expenditure assessed within the robustness and efficiency of cost gate is £1.170m which is comprised of the following: - Resilience schemes £1.170m (schemes 1, 6a and 7), the company’s proposed capital programme, including the resilience programme has been externally assured. It states use of cost estimates based on ‘consultant and independent quantity surveyor estimates’ and costs ‘appear to be reasonable with appropriate allowances for overheads and contingency’ (Reference Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit p.g. 3, 8). The company has also provided a breakdown of costs in spreadsheet format a comparison of some unit rates used found these to be within a reasonable range (S795_MS003.xlsx, Appendix 6: MS003 &MS006a Cost build-up; MS001 cost build up; MS007 cost build-up). The scheme passes efficiency on this basis. 'Scheme 3' has not been assessed at draft determination as it has not passed the needs gate. Resilience studies has not been assessed in this gate at draft determination as it has not passed the needs gate. The total investment passed within the gate is £1.170m | - Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit - S795_MS003.xlsx - Appendix 6: MS003 &MS006a Cost build-up – Network Support for Farlington and Gosport Zones - MS001 show cost build up for scheme VOC monitors - MS007 show cost build-up for scheme – Nelson to Lovedean Strategic Support Cost sheet | Robustness and efficiency of costs | Pass | The companies proposed capital programme, including the resilience programme have been externally audited by Atkins (Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit). The audit states that costs were based on "Project estimates based on consultant and independent QS estimates." (Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit, p3). The company has also provided a breakdown of costs for the proposed schemes in spreadsheet format a comparison of some unit rates used found these to be within a reasonable range (S795_MS003.xlsx, Appendix 6: MS003 &MS006a Cost build-up – Network Support for Farlington and Gosport Zones) The company has presented some evidence of a range of options selected and selection of the most cost beneficial option in the Unit Cost row of 9.5.7 S795.PPA.1102 (p3-5). Overall, the evidence provided was considered sufficient. | Appendix 7: DG026_SAF Capital Programme_V4.doc – Capital Programme Summary of Audit, p3 S795_MS003.xlsx, Appendix 6: MS003 &MS006a Cost build-up – Network Support for Farlington and Gosport Zones 9.5.7 S795.PPA.1102
Customer protection | Pass | As the company has not raised substantive issues in its representation and we allow no further expenditure, we retain our draft determination assessment regarding this gate. | PR19 DRAFT DETERMINATION REPRESENTATION FINAL Appendix 3.2.1a Resilience Study Appendix 3.2.1b Quay Rd | Customer protection | Pass | Customer protection is considered sufficient. There is a bespoke performance commitment relating to the 'Resilience schemes' which requires on time completion of the proposed schemes by 2024/2025. We note the disallowance of 'scheme 3 - supply deficit Farlington' expenditure. The performance commitment is reputational only (Reference Portsmouth Water Business Plan 2020-2025, September 2018, p.g. 48). Considering the scale and nature of the investment, customer protection is sufficient. | Appendix 3.10 Performance Commitments Definitions, September 2018, p.g. 24 Portsmouth Water Business Plan 2020-2025, September 2018, p.g. 39-40 | Customer protection | Pass | The company proposes the common resilience PCs and 2 bespoke resilience PCs with non-financial incentives that are related to security of water supply.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A
Further analysis / arguments
Further analysis / arguments
AMP7_PPA_1105 - Strategic Mains Support was reallocated to line 11 New developments because the need clearly related to preparing for expected growth of new developments..
Scheme Requested Allowed
AMP7_PPA_1101 - Resilience Studies v2 30Jan2018 £74.9k £74.9k
AMP7_PPA_1102 - Resilience Schemes V5 30Apr18 £2,472.7k £2,472.7k

## Deep dive SES
FD - Deep dive sheet - SES Water |  |  |  | DD - Deep dive sheet - SES Water |  |  |  | IAP - Deep dive sheet - SES Water
Summary at FD |  |  |  | Summary at DD
Company | SES |  |  | Company | SES
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 8.866 |  |  | Totex carried through deep dive AMP7 (£m) | 8.866 |  |  | Summary at IAP
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 8.866 |  |  | Totex assessed within deep dive (£m) | 8.866
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 6.3749 |  |  | Totex allowance from deep dive (£m) | 0 |  |  | Expenditure carried through deep dive AMP7 (£m) | 8.868
Ofwat view of totex allowance for AMP7 (£m) | 6.3749 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 0 |  |  | Ofwat view of allowance for AMP7 (£m) | 8.057
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | The company makes representations for us to accept its ‘Resilience enhancement programme’ investment (£8.9m). The company demonstrates that the investment aims to complete the provision of second source of supply for customers in all of its operational areas, started ten years ago (and funded in 2005-10 and 2010-15 as part of a 15-year enhancement programme). It provides additional evidence to support the investment in relation to potential asset failures affecting 67,000 customers in areas currently without alternative supply. Although a number of risks presented are outside of resilience enhancement scope (e.g. terrorism), for the other risks (e.g. asset failures due to third party damage) the company provides evidence of management control measures, probability, consequence and potential funding sources. The company also explains how the investment is complementary to the wider WRMP framework as it can potentially support drought resilience improvements beyond 1 in 200 year events and proposals for regional strategic transfers in the future. The investment is partially accepted, including: upgrades to Bough Beech WTW (£3.094m), pump upgrades (£3.444m) and strategic main (£1.850). However, the element of the investment to provide by-passes around service reservoirs where none currently exist (£0.480m) is not accepted as this is related to maintenance issues and unrelated to the resilience risks considered in the failure mode assessment tables. The total value of the investment accepted within the need gate for final determinations is £8.388m. | SES Water response to draft determination 30 August 2019 A.DD.OC3 Representation on resilience enhancement expenditure | Need for investment | Fail | The total investment assessed within the water resilience enhancement line is £8.870 m (all capex) which is comprised of the following: - Bough Beech and pump station upgrades (£6.538 m) - No allowance is made for this investment as there is insufficient evidence to demonstrate the need to invest in enhanced resilience for customers. The investment is for upgrades to Bough Beech pumping station in the South of the company's region and booster pumping station upgrades to allow transfer of water from Bough Beech towards the north of the company's region. Bough Beech is a river source whereas existing sources of supply in the north are from groundwater. The company advises that the upgrades are required to supply customers in the north from an alternative source in the scenario of a 1 in 200 groundwater drought or works outage. The company advises that the investment is 'paramount to the delivery of its drought plan and WRMP'. However, within the company's revised draft WRMP there is no evidence that supply side solutions are required to mitigate 1 in 200 drought risk throughout the 2020-80 planning period. Instead the risk is mitigated by the company's proposed increased ambition for its demand side solutions. The company's proposed low probability failure modes that would result in works outage are insufficiently specific (eg 'catastrophic asset failure'), are funded through other areas of enhancement such as SEMD (eg 'terrorist attack') or result in consequences for which the company provides no evidence of management control (eg '3rd party damage to distribution main'). - Network enhancement £2.330m - No allowance is made for this investment as there is insufficient evidence to demonstrate the need to invest in enhanced resilience for customers. The investment is for construction of a new main from How Green to Langley Park reservoir to ‘provide enhanced resilience in the event of an outage of service reservoirs where currently an outage of the reservoir would result in the loss of supply to customers'. The company's proposed low probability failure modes that would result in outage are insufficiently defined, are funded through other areas of enhancement such as SEMD (eg 'terrorist attack') or result in consequences for which the company provides no evidence of management control (eg '3rd party damage to distribution main'). Following our initial assessment of business plans we indicated that we would make allowances for these investments. During the time intervening between our initial assessment and draft determinations we have considered the evidence presented by the company in more detail and no investment is passed through the need for investment gate. | Our business plan for 2020-2025, p103-105 WRMP planning tables | Need for investment | Partial pass | The projects considered are clearly linked to removing risks of single supplies with the aim of having 100% of properties being able to be supplied by more than one treatment works (BP, Chapter 4, p103-104). This is consistent with our view of resilience investment. | BP, Chapter 4, p103-104
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A
Best option for customers | Fail | The total expenditure assessed within the options gate is £8.338m. We apply a 20% optioneering challenge to the accepted investment, as the company fails to provide any evidence regarding alternative options to the preferred solution. The total value of the investment accepted within the best option for customers gate for final determinations is £6.666m. | SES Water response to draft determination 30 August 2019 A.DD.OC3 Representation on resilience enhancement expenditure | Best option for customers | Not assessed |  |  | Best option for customers | Pass | The company identifies network resilience as a main priority for customers (BP, Chapter 1, p31) and have stated they have chosen the most efficient options based on the latest data available to them. However, there is limited detail provided on what options have been evaluated. (BP, Chapter 4, p104) | BP, Chapter 4, p104
Robustness and efficiency of costs | Fail | We apply a company specific efficiency challenge to the passed investment, as the company fails to provide concrete evidence of efficient costs. The company states that this is the most efficient part of the programme since “the most challenging aspects of the scheme have already been completed”. However, the company does not support its views with concrete comparative evidence on specific costs, such as benchmarks or third party audits. The total investment passed within the gate is £6.375m. | SES Water response to draft determination 30 August 2019 A.DD.OC3 Representation on resilience enhancement expenditure | Robustness and efficiency of costs | Not assessed |  |  | Robustness and efficiency of costs | Pass | The company states that it has used a number of sources including framework rates, schedule rates and common costs. The plan splits out costs for each intervention for each year between 2020-25. The costs for each intervention were also reviewed by cost consultants. (BP, Chapter 4, p106). | BP, Chapter 4, p106
Customer protection | Pass | The need for customer protection against non-delivery has been assessed for the allowed schemes. This is covered by a bespoke performance commitment ‘Risk of supply failures’. The PC has an underperformance ODI attached to it, which protects costumers from the company not delivering the accepted schemes. The customer protection is appropriate. | SES Water response to draft determination 30 August 2019 A.DD.OC3 Representation on resilience enhancement expenditure | Customer protection | Not assessed |  |  | Customer protection | Pass | The company has put forward a performance commitment with a financial penalty for not delivering on the target of a 100% of properties being able to be supplied by a second supply by 2025 (BP, Chapter 4, p106). | BP, Chapter 4, p106
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A

## Deep dive SEW
FD - Deep dive sheet - South East Water |  |  |  | DD - Deep dive sheet - South East Water |  |  |  | IAP - Deep dive sheet - South East Water
Summary at FD |  |  |  | Summary at DD
Company | SEW |  |  | Company | SEW
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 33.9605 |  |  | Totex carried through deep dive AMP7 (£m) | 33.9605 |  |  | Summary at IAP
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 33.9605 |  |  | Totex assessed within deep dive (£m) | 33.9605
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0 |  |  | Expenditure carried through deep dive AMP7 (£m) | 1.3205
Totex allowance from deep dive (£m) | 10.8607 |  |  | Totex allowance from deep dive (£m) | 3.53
Ofwat view of totex allowance for AMP7 (£m) | 10.8607 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 3.53 |  |  | Ofwat view of allowance for AMP7 (£m) | 1.309
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | See below for our assessment, the text of which does not fit in the one cell. | Chapter 3 Securing cost efficiency FINAL Query SEW-FD-CE-001, October 2019 Query SEW-FD-CE-002, October 2019 | Need for investment | Partial pass | The total expenditure assessed within the resilience water enhancement line is £33.961m (all capex) and comprises of the following: - Flooding at production sites £1.300m, pass. This investment links to the definition of this line to protect against 0.1% (1-1000 year) annual exceedance probability flood resilience based on the National Flood Resilience Review. The company has provided its analysis of how flood risk at sites has been assessed and that it has taken into account criticality. The investment mitigates flood risk at 92 production sites and pumping stations (Appendix 9, p.g. 86-90). - Strategic mains resilience £19.060m, passing 1 of 3 schemes - £2.230m is passed (References Chapter 4, p.g. 46-52; Query SEW-DD-CE-005) (1) Arlington WTWs to Windover secondary source of supply £2.230m is passed. The existing supply main is from Deep Dean WTWs to Windover Reservoir is a single source of supply risk for 1,722 properties in a remote part of South Down National Park. The company has demonstrated that risk of mains failure is high consequence and low probability. Topographical constraints restrict the ability to respond and repair the main in a timely manner, resulting in customer water supply interruption after 48hrs. The mains failure and interruption of supply is thus considered beyond company control. Providing a secondary source of supply from Arlington WTWs to Windover Reservoir is justified. (2) Wellwood Reservoir to Potters Corner Reservoir secondary source of supply £7.480m is failed. Potters Corner Reservoir is supplied by 4 water treatment works, considered by the company to be an ‘equivalent single source of supply’ to approximately 33,000 customers. Mains failure to Potters Corner Reservoir is identified as the key risk however there is evidence that the burst rate is a frequent/ persistent problem and therefore we do not consider it to be resilience enhancement expenditure. The company provides little or no evidence that it is beyond management control to restore water supply to customers before significant supply interruption occurs. (3) Greywell Reservoir to Cliddesden Reservoir secondary source of supply £9.350m is failed. Cliddeden Reservoir is supplied by 3 water treatment works to provide water supply for approximately 20,000 customers. Mains failure is identified as the key risk however there is evidence that the burst rate is a frequent/ persistent problem that cannot be considered resilience enhancement. The company provides little or no evidence that it is beyond management control to restore water supply to customers before significant supply interruption occurs. - Barcombe Water Treatment Works (WTWs) additional treatment £11.200m, is failed. The investment at Barcombe WTWs provides resilience against supply interruptions during an outage at the treatment works caused by failure or inability to take the contact tank out of service for maintenance. Barcombe WTW has two process streams, 'stream 1' has insufficient capacity to supply customers in the event of a 'stream 2' outage. The investment is to increase the treatment capacity of stream 1 so that supply can be maintained during failure or maintenance outage of stream 2. The company indicates failure could be caused by raw water intake main or pump and that there is insufficient flexibility to take the 'stream 2' contact tank out of service for planned maintenance. It states that in the event of failure, supply to 50,000 properties would be lost after 5 days during average peak week demand. No evidence is provided that failure or maintenance would result in outage duration that would exceed 5 days and result in supplies being lost. The ability for the system to cope for 5 days during peak before supplies are lost raises doubt this is a genuine single source of supply risk. It states that following the improvements the plant would be resilient to unexpected extreme events, however there is no evidence of any specific extreme events or the likelihood of failure being low. South East Water has not sufficiently demonstrated that failure (or maintenance) and the consequence is beyond company control to manage. (Chapter 4, p.g. 34-43). - Oakhanger Water Treatment Works (WTWs) additional storage £2.400m, is failed. It is proposed to increase capacity of contact tank at the WTW through a new storage tank to improve operational resilience of the 626 pumped network. The company acknowledges that this ‘is an ongoing issue during periods of high demand, rather than a low probability, high impact event, and relates to one of the underlying issues with operating a pumped system’. The WTWs has a lack of capacity to cope during peak demand periods (citing summer heat waves) if there is an operational issue at the site. This is a known capacity constraint and is not related to a low probability high consequence event. (Chapter 4, p.g. 43-46). The total investment passed within the gate is £3.530m. | South East Water Business Plan, Resilience in the Round Appendix 9, September 2019, p.g. 86-90 South East Water IAP Response – Securing long term resilience, April 2019. Chapter 4 p.g. 46-52, p.g. 34-43, p.g. 43-46. Query SEW-DD-CE-005, May 2019 | Need for investment | Partial pass | Overall SEW have allocated its resilience spend between 3 areas, these include: Investment for Flood protection (£1.35m) links to the definition of this line to protect against 1-1000 flood resilience based on the NFFR (Appendix 9, s8.1.2, p86). The company has provided its analysis of how flood risk at sites has been assessed and that it has taken into account criticality. (Appendix 9, p87-90) The strategic mains resilience (£21.11m) seek to improve interconnectivity to reduce risk of supply interruptions and single sources of supply. This programme failed to provide sufficient evidence of how each scheme resolved a single source of supply issue or mitigates against low probability high magnitude events. The analysis considers the position after 5 days after "reasonable mitigation actions" have been implemented but does not state why this is an appropriate time period or what mitigation options were considered. This investment has been assessed as base expenditure. The programme to increase capacity / redundancy at WTW (11.82m) has been identified to mitigate the risk of supply interruptions when one of the 2 single cell contact tanks are out of service. Further evidence would need to be provided identifying how the risk relates to unexpected low probability, high impact events and that other alternative options have been considered to manage this risk and why current management options that have been used to manage this risk are no longer sufficient. Without such evidence the scheme costs has been assessed as base expenditure. | Appendix 9, s8.1.3
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A | NA
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A | NA
Best option for customers | Pass | The investment assessed within the best option for customers gate is £11.835m. - Wellwood service reservoir to Potters Corner service reservoir secondary source of supply £7.480m: We pass this investment. South East Water provides evidence that it has considered alternative supply routes for a new main which is more expensive than the solution proposed. Options to address the turbidity (microfiltration) are not considered because they do not address the risk of mains failure. Management methods such as demand management, tankering, bottles/bowsers, catchment management are also considered in the options analysis and are deemed insufficient or are discounted. - Barcombe water treatment works additional treatment £0.825m. We pass this investment. South East Water provides evidence that it considers alternative water treatment work options that are more expensive than the proposed solution and we also acknowledge the significantly reduced scope that we establish in the needs gate. - For ‘Flooding at production sites’ (£1.300m) and Arlington water treatment works to Windover service reservoir secondary source of supply £2.230m, the company has not raised substantive issues in its representation and we retain our draft determination assessment to pass these investments in this gate. The investment we pass within the gate is £11.835m. | Chapter 3 Securing cost efficiency FINAL Query SEW-FD-CE-001, October 2019 Query SEW-FD-CE-002, October 2019 | Best option for customers | Pass | The total expenditure assessed within the options gate is £3.530m which is comprised of the following: - Flooding at production sites £1.300m, pass. Costs are developed for different interventions based on risk category and site specific considerations including accessibility during flooding. The options are focused on flood resistance mitigations with consideration of network back-up supply and equipment redundancy. The company has shown that the site interventions have a large positive benefit to cost ratio regardless of being single source of supply sites or sites with a duplicated source of supply (Appendix 9, p.g. 87-92). - Strategic mains resilience (Arlington WTWs to Windover Main only) - £2.230m, pass - The solution has been shown to have a positive benefit to cost ratio. The Arlington Windover main has assessed alternative options and chosen the lowest cost option (IAP Response Chapter 4, p.g. 47-48) The total investment passed within the gate is £3.530m | South East Water Business Plan, Appendix 9, September 2019, p.g. 87-92 South East Water IAP Response – Securing long term resilience Chapter 4, April 2019 p.g. 47-48. | Best option for customers | Pass | The evidence provided was considered sufficient for the flood protection schemes. This included details of costs as assessed below for different interventions based on risk category and consideration of different options including do-nothing options and adding duplicated sources of supply. The company have shown that all options considered had large benefit to cost ratios. | Appendix 9, s8, p97-98
Robustness and efficiency of costs | Partial pass | The investment assessed within the robustness and efficiency of cost gate is £11.835m. - Flooding at production sites £1.300m. As per draft determination we do not apply the company efficiency challenge. -Arlington water treatment works to Windover service reservoir secondary source of supply £2.230m: We pass this investment, as per draft determination. We note our mistake in referencing Portsmouth Water in our draft determination - this should have stated South East Water. - Wellwood service reservoir to Potters Corner service reservoir secondary source of supply £7.480m: We apply an efficiency challenge to this investment. South East Water states that it has used its unit cost database (UCDB) and programme costing and estimate tool (PCET). These costs have been built up over previous price reviews and utilise historical scheme costs, supplier data and standard pricebook data (Appendix 9, s8.1.1, p85). South East Water reduces its costs for the investments by 9.7% from a pre-efficiency level, but there is no evidence of a cost breakdown or cost model to establish that the pre-efficiency or post-efficiency level of expenditure is efficient. We undertake a unit cost comparison to a similar pipeline investment and consider this investment to be a high cost. Applying benchmark unit rate per meter cost of £0.722m/km, we estimate a total cost of the 15km main to be £10.843m. As per South East Water’s programme, we are funding 60% of this to be completed in 2020-25 with an allowance of £6.506m. The remaining 40% of funding £4.337m should be requested in the 2025-30 period. - Barcombe water treatment works additional treatment - £0.825m: We pass this investment. We consider the cost estimate provided and confirm the use of the unit cost database in building up the cost estimate and the reasonable allocations between items, direct and indirect costs. The total investment allowance is £10.861m, which includes the additional £7.331m which we now pass at final determination. | Chapter 3 Securing cost efficiency FINAL Query SEW-FD-CE-001, October 2019 Query SEW-FD-CE-002, October 2019 | Robustness and efficiency of costs | Pass | The total expenditure assessed within the robustness and efficiency of cost gate is £3.530m which is comprised of the following: - Flooding at production sites £1.300m, pass - The company has stated it has used its Unit Cost Database (UCDB) and Programme Costing and Estimate Tool (PCET). These costs have been built up over previous price reviews and utilise historical scheme costs, supplier data and standard pricebook data (Appendix 9, p85, p93). For the flood resilience schemes details on the average costs of mitigation and details of extrapolation have been presented and how costs have been applied against different levels of risks (Appendix 9, Table 23, p92). Costs have been reduced from £1.350m in the September 2018 submission to £1.300m in the April 2019 submission, a 4.7% reduction (IAP Response Chapter 4, p.g. 21). - Strategic mains resilience (Arlington WTWs to Windover Main only) - £2.230m, pass. The company has stated it has used its Unit Cost Database (UCDB) and Programme Costing and Estimate Tool (PCET). These costs have been built up over previous price reviews and utilise historical scheme costs, supplier data and standard pricebook data (Appendix 9, s8.1.1, p85). Portsmouth Water has reduced costs for the schemes by 9.7%, costs in the September 2018 submission costs were £21.110m in total and in the April 2019 they are now £19.060m (IAP Response Chapter 4, p.g. 21). The total investment passed within the gate is £3.530m | South East Water Business Plan, Resilience in the Round Appendix 9, September 2019, p.g. 85, 93 South East Water IAP Response – Securing long term resilience Chapter 4, April 2019. p.g. 21. | Robustness and efficiency of costs | Pass | The company has stated it has used its Unit Cost Database (UCDB) and Programme Costing and Estimate Tool (PCET). These costs have been built up over previous price reviews and utilise historical scheme costs, supplier data and standard pricebook data (Appendix 9, s8.1.1, p85). For the flood resilience schemes details on the average costs of mitigation and details of extrapolation have been presented and how costs have been applied against different levels of risks (Appendix 9, Table 23, p92). | Appendix 9, p85-86, p89-92
Customer protection | Partial pass | In addition to the customer protection for the ‘flooding at production sites’ investment which has a performance commitment ‘company sites protected from risk of flooding’ (PR19SEW_B.4). We consider customer protection for the additional investments allowed at final determination. We apply a performance commitment to the ‘Wellwood service reservoir to Potters Corner service reservoir’ investment to protect customers against non-delivery. We acknowledge South East Water does not consider it appropriate to apply a performance commitment to this investment based on progress and is proposing annual reporting only but we consider it necessary to incentivise delivery. In particular, we consider it necessary because this investment is funding only 60% of the main and the remaining 40% will be completed in the 2025-2030 period. Further details of the performance commitment and outcome delivery incentive can be found in the final determination outcomes documentation. | Chapter 3 Securing cost efficiency FINAL Query SEW-FD-CE-001, October 2019 Query SEW-FD-CE-002, October 2019 | Customer protection | Pass | Customer protection is satisfactory. The company includes the range of common resilience and asset health performance commitments designed to incentivise resilience. The company has a performance commitment directly related to the flood resilience scheme 'Company sites at risk of flooding' which protects against non-delivery, it has an end of period underperformance penalty if 92 sites are not protected. The company has not proposed a specific performance commitment associated with the delivery of the 'Strategic mains resilience' scheme, given the scale and nature of the allowed scheme this is considered appropriate. | South East Water IAP Response – Securing long term resilience Chapter 4, April 2019. p.g. 21. | Customer protection | Pass | The company includes the range of common resilience and asset health PCs designed to incentivise resilience. The company has not proposed a specific PC associated with the delivery of the resilience enhancements, given the scale and nature of the schemes this is considered appropriate.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A | NA
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A | NA
Need for investment: South East Water submits representations on our draft determination regarding: ‘Wellwood service reservoir to Potters Corner service reservoir’; ‘Greywell service reservoir to Cliddesden service reservoir’; ‘Barcombe water treatment works additional treatment’; and ‘Oakhanger water treatment works additional storage’, claiming the same amount as in April 2019, that are assessed below. The total amount we assess within the needs gate is £33.961m (all capex). Strategic mains resilience (£19.060m) comprises 3 water main investments. The decision to pass the investment for (1) Arlington WTWs to Windover secondary source of supply (£2.230m) remains unchanged as per draft determination. The company does not raise substantive issues regarding this investment. We consider the representation the company makes on (2) Wellwood service reservoir to Potters Corner and (3) Greywell water treatment works to Cliddesden service reservoir. (2) Wellwood service reservoir to Potters Corner service reservoir secondary source of supply (£7.480m): Having reviewed the representation provided to us, we consider the evidence sufficient and convincing in regard to the high consequence low probability risk of mains failure lasting 36 hours that would result in an extended duration supply interruption for 29,000 customers supplied by Potters Corner service reservoir. The company’s evidence supports the claim that mains failure is low probability with a mains failure rate that is much lower than the level for intervention and that the duration of failure could be 36 hours with critical asset crossings on the main causing high consequence water supply interruption. We consider the evidence in regard to the growth funding allowance for ‘Godmersham to Potters Corner’ main and Aldington service reservoir. We are sufficiently convinced that a residual risk (main failure) remains which could cause a high consequence supply interruption to customers supplied by Potters Corner service reservoir. The risk of groundwater turbidity causing water treatment plant outage has not been a factor in our decision to allow this investment as we are not sufficiently convinced that the risk is plausible or beyond management control. The water treatment works supplying Potters Corner only had short duration outages caused by turbidity in the past and it is induced by higher abstraction rates which is manageable to some extent. Based on the evidence of the mains failure risk we pass the investment to complete 60% of the 15km main in the 2020-25 period, with the remaining 40% investment £4.987m to be completed in 2025-30 period. The total investment cost for the 15km main is £12.467m with a target completion by October 2026 (18 months after 2020-25 period) based on the programme provided by South East Water. (3) Greywell service reservoir to Cliddesden service reservoir secondary source of supply (£9.350m): We do not make an allowance for this investment based on the representation South East Water makes at final determination. The company provided insufficient and unconvincing evidence that a 48-hour repair time is plausible on the mains supplying the reservoir or that the duration of supply interruption would be significant for customers as Cliddesden service reservoir will still have a water main supplying it if one of the mains fails. The company justifies the 48-hour repair time on basis of the PVC and cast iron mains being large diameter and large excavation being required to repair a longitudinal failure on the PVC main. We consider the repair time excessive; the mains are not particularly large diameter, the depth of the main is not discussed, and there is no evidence of critical crossings along the main. In addition, we consider that the risk of water treatment plant outage described by the company is insufficient to cause significant water supply interruption, given that failure modes discussed (water quality etc.) are largely within management control and the maximum outage duration has been 26 hours. - Barcombe water treatment works additional treatment (£11.190m): We pass £0.825m of this investment through the need gate based on the representation South East Water makes at final determination. We consider that the evidence to mitigate a single point of failure risk associated with the contact tank on treatment stream 2 is sufficient and convincing. We consider there is a risk of contact tank failure that will cause significant water supply interruption to customers receiving water from Horsted Keynes service reservoir. This is because Horsted Keynes service reservoir can currently only receive water supply from treatment stream 2, and therefore if the single cell contact tank fails on treatment stream 2, the supply to Horsted Keynes service reservoir will be lost. The other service reservoirs that Barcombe water treatment plant supplies - St Francis, Popeswood and Uckfield - can be supplied from both treatment streams. To mitigate this risk, we accept the £0.825m investment for a cross connection between the two treatment streams and the upgrade of the high lift pump station on treatment stream 1 which allows treatment stream 2 to divert to the contact tank on treatment stream 1 bypassing a contact tank 2 failure and to supply Horstead Keynes service reservoir from both treatment streams. We determine that this will alleviate the single point of failure risk and ensure all service reservoirs dependent on the water treatment works to be supplied from both treatment streams under average demand conditions (35ML/day). However, we consider that the demand scenarios, failure modes (maintenance backlog, reduction of deployable output due to planned maintenance) and increasing stresses (increasing demand, complexity etc.) presented by the company for the water treatment works are not necessarily associated with high consequence-low probability events that are beyond management control. In particular, the investment to upgrade treatment stream 1 (to 35ML/day) and duplicate the contact tank on treatment stream 2 is related to process maintenance and capacity constraints for which the company receives a base allowance. The investment is therefore not accepted as a resilience enhancement. - Oakhanger water treatment works additional storage (£2.390m): We make no allowance for this investment based on the representation South East Water makes at final determination. We consider the evidence and conclude that this investment is mitigating an ongoing issue during peak demand events associated with insufficient capacity of the contact tank at the Oakhanger water treatment works (and storage capacity in the network) and is not a high consequence-low probability event. The low capacity of the contact tank means there is insufficient time to undertake maintenance and respond to breakdowns and failures before supply can be restored. The company states that the unavailability of Oakhanger water treatment works will result in low pressure to 4,000 customers which we do not consider a high consequence water supply interruption. The investment is considered to be associated with a lack of capacity/redundancy to undertake maintenance of the works for which the company receives a base allowance. The risk of failure of other critical assets in the system has no evidence to support the case. - Flooding at production sites £1.300m: The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. We pass £1.300m. The investment we pass within the gate is £11.835m, which includes the additional £8.305m which we now pass at final determination.
Further analysis / arguments
Scheme Requested Allowed
Flood protection schemes £1.35m £1.35m
Strategic mains resilience £21.11m £0m
Increase capacity at WTW to provide redundancy £11.82 £0m

## Deep dive SSC
FD - Deep dive sheet - South Staffs Water |  |  |  | DD - Deep dive sheet - South Staffs Water |  |  |  | IAP - Deep dive sheet - South Staffs Water
Summary at FD |  |  |  | Summary at DD
Company | SSC |  |  | Company | SSC
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 4.1012 |  |  | Totex carried through deep dive AMP7 (£m) | 4.1012
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0
Totex assessed within deep dive (£m) | 4.1012 |  |  | Totex assessed within deep dive (£m) | 4.1012 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 1.8729 |  |  | Totex allowance from deep dive (£m) | 0.37975 |  |  | Expenditure carried through deep dive AMP7 (£m) | 4.1475
Ofwat view of totex allowance for AMP7 (£m) | 1.8729 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 0.37975 |  |  | Ofwat view of allowance for AMP7 (£m) | 3.862
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | We note the withdrawal of Lammas crossing (strategic Cam River crossing) investment and no evidence of representation for the ‘Perry Bar transfer’ investment which accounts for the reduction in the requested investment from £3.100m to £2.395m. South Staffs Water submits representations on our draft determination regarding: ‘Network resilience’ and ‘Borehole installation’ claiming a lower amount as in April 2019, that are assessed below. The total amount we assess within the needs gate is £3.407m (all capex). - Network resilience £2.395m – we consider the representation South Staffs Water makes at final determination and pass £0.982m for 3 of the 5 investments. We pass the investment for Norman Road pump station (£0.069m), Town Gate (£0.445m) and Caxton-Gibbet to Papworth (£0.468m). We have reviewed the evidence and consider there is sufficient and convincing evidence that these investments meet our criteria in regard to being high consequence (in terms of customers impacted and supply interruption duration) and the low probability (mains failure likelihood is sufficiently low) events with factors that are beyond management control (e.g. access restrictions, no storage). Norman Road pump station risk is being mitigated via a network interconnection, Town Gate and Caxton-Gibbet to Papworth risks are mitigated via duplication of the supply mains. The investments for Bourn Tower (£0.410m) and All Saints Way (£1.003m) do not pass our assessment criteria as we do not consider that the risks will result in a high consequence water supply interruption that is beyond management control: a 12 hour failure of the main supplying Bourn Tower does not result in a long duration supply interruption with supply being maintained to customers from the tower for approximately 8 hours. Failure of mains at All Saints Way causes a supply interruption between 3 and 12 hours and low pressure. - Borehole installation £0.612m. We pass £0.560m. We consider the representation South Staff Water makes and the evidence sufficiently demonstrates that there is a low probability-high consequence risk of supply interruption to customers in the Cambridge area during dry annual average conditions. One of the largest three borehole sites could be lost for a duration of up to 3 months due to turbidity or pollution events, in particular the loss of the largest borehole site Fleam Dyke (15.6ML/day). In addition to the evidence presented, we consider South Staff Water’s water resources management plan which confirms the insufficient headroom to cover the loss of the largest site during dry annual average conditions. Our decision to allow this investment is not based on peak conditions, the water resource management plan indicates sufficient headroom to cover the loss of the largest borehole. Considering the cost breakdown provided for this investment, we do not allow £0.052m to ‘abandon existing borehole’, as this funding is for a new borehole, not to replace an existing borehole which would otherwise be considered to be funded as a base renewal cost. Power resilience £0.400m, we pass this investment as per our draft determination. The investment we pass within the gate is £1.942m, which includes the additional £1.542m which we now pass at final determination. | Response to Ofwat's draft determination on our business plan for 2020 to 2025 | Need for investment | Partial pass | The total expenditure assessed within the resilience water enhancement line is £4.101m (all capex) and comprises of the following: - Power resilience and borehole installation £1.000m - £0.400m is passed for the 'power resilience' component, this investment mitigates against power outage and the ability to transfer water and supply customers by investing in on site power generation for booster pump stations. The component of investment relating to 'borehole installation' is not accepted. This reduction in allowance since IAP is based on the provision of more detailed information by the company at draft determination and the application of a refined acceptance criteria for resilience enhancement which is described in the model cover sheet. There is insufficient evidence provided to demonstrate that this is a high consequence - low probability risk or that this risk is beyond the company's control to manage. There is little or no evidence of the specific cause of failure ‘borehole failure’ is very general and vaguely defined: the duration of failure is stated as ‘more prolonged than other types of failures’; and the likelihood of failure is ‘relatively low’. The ‘surplus remaining if site is lost' figures provided indicate that the peak demand shortfall is marginal even if a borehole site is lost due to asset failure (Reference Query SSC-DD-CE-004). - Network resilience £3.100m, the need is failed, it is considered to be base investment. Our decision to make no allowance for this scheme at draft determination (following an initial allowance at IAP) is based on the provision of more detailed information by the company at draft determination and the application of a refined acceptance criteria for resilience enhancement which is described in the model cover sheet. Six individual strategic interventions are part of this scheme. There is insufficient evidence to demonstrate that the cause of failure and the impact is beyond the company's control to manage. There is also doubt in the ‘River Cam strategic crossing’ case that the solution will mitigate the risk sufficiently. The risk is insufficiently quantified and vaguely defined: the number of customers is specified however the duration of interruption is minimal or not specified; and the likelihood of failure is specified as ‘low’ with no evidence to support this (Reference Query SSC-DD-CE-004). Norman Road Pump Station case study states there have been numerous unplanned outages 30mins to 3hrs in duration (Refer Appendix A29, pg. 24). The total investment passed within the need for investment gate is £0.400m. | Query SSC-DD-CE-004 Appendix A29 Capital investment to deliver a class leading service, Sep 2018 | Need for investment | Partial pass | SSC proposes 3 schemes within its water resilience enhancement programme. The scheme to reintroduce groundwater sources has been reallocated to supply-side investments for supply and demand balance as the need presented stated that the schemes would help meet overall supply demand balance (Appendix A29, s3.2.2, p74). The schemes to address power supply issues (£1m) is appropriate to this area. The company have clearly identified and assessed risks of low probability-high consequence external power outages. The risk has been upgraded following an external assessment (National Risk Assessment, 2017) and leading to the need to upgrade resilience to power supplies. (Appendix A29, s3.2.2, p70-71) The need for the network resilience scheme (£3.1m) is also accepted as the risks identified are related to single sources of supply and points of failure (Appendix A29, s3.2.2, p76). | Appendix A29, s3.2.2, p70-76
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A
Best option for customers | Pass | The investment assessed within the best option for customers gate is £1.942m. - Network resilience £0.982m. South Staffs Water has completed modelling and options assessment at a network level and selected the most cost effective and beneficial schemes. A cost benefit appraisal undertaken as part of the investment optimisation process meant choosing the most cost-effective solutions for customers (Appendix A29, s3.2.2, p76). No further evidence is provided on options or cost benefit analysis of alternatives, however we consider the solutions as appropriate considering the low materiality of the investments. We do not apply an optioneering challenge. - Borehole installation £0.560m. South Staffs Water has provided sufficient evidence that options have been considered appropriately. We consider that South Staffs Water has completed modelling and options assessment at a network level and selected the most cost effective and beneficial schemes. A cost benefit appraisal undertaken as part of the investment optimisation process meant choosing the most cost-effective solutions for customers (Appendix A29, s3.2.2, p76). South Staffs Water considers alternative licence abstraction and alternative sources which are currently not viable. The company proposes to consider future duplication of boreholes and alternative water supply options to further mitigate this risk. We do not apply an optioneering challenge. Power resilience £0.400m. We pass this investment as per our draft determination. The investment we pass within the gate is £1.942m. | Response to Ofwat's draft determination on our business plan for 2020 to 2025 | Best option for customers | Pass | The total expenditure assessed within the options gate is £0.400m which is comprised of the following: - Power resilience and borehole installations (assessment of 'power resilience' component only) £0.400m, pass. The company completed modelling and options assessment at a network level and selected the most cost effective and beneficial schemes. A rationale for the schemes and why they are the most suitable option for customers, including identifying that the cost benefit appraisal undertaken as part of the investment optimisation process meant choosing the most cost-effective solutions for customers (Appendix A29, s3.2.2, p76). No further evidence is provided on options or cost benefit analysis in the April 2019 submission, however consideration is given to the low materiality of the scheme. Our assessment at this gate remains unchanged from the IAP, however we acknowledge that we incorrectly assigned the status of this gate as ‘Partial Pass’ at that time. As ‘network resilience’ has not passed the needs gate, it has not been assessed. The total investment passed within the gate is £0.400m. | Appendix RA02 - Addendum to appendix A29 – wholesale water enhancement cost allowance, April 2019. Appendix A29 Capital investment to deliver a class leading service, Sep 2018 | Best option for customers | Partial pass | The company provides a rationale for each of the accepted schemes and why they are the most suitable option for customers, including identifying that the cost benefit appraisal undertaken as part of the investment optimisation process meant choosing the most cost-effective solutions for customers. Further detail on the optioneering could have been provided, e.g. further details on alternatives and comparative benefits. (Appendix A29, s3.2.2, p76) | Appendix A29, s3.2.2, p70-77
Robustness and efficiency of costs | Partial pass | The investment assessed within the robustness and efficiency of cost gate is £1.942m. Network resilience £0.982m. We do not pass this investment. South Staffs Water states that its costs are built up from bottom up quantity surveying rates, scopes of works have been challenged and projected efficiencies applied to scheme costs. (Appendix A29, s3.2.2, p77). No cost breakdown or cost model has been provided to evidence this investment is efficient. We therefore apply the company specific efficiency challenge. Borehole installation £0.560m. We pass this investment. South Staffs Water states that its costs are built up from bottom up quantity surveying rates, scopes of works have been challenged and projected efficiencies applied to scheme costs. (Appendix A29, s3.2.2, p77). A cost breakdown has been provided based on a consultant cost model which confirms costs are efficient. Power resilience £0.400m. We maintain our decision at draft determination not to pass this investment on robustness and efficiency of cost. South Staffs Water provides no representation evidence in regard to our decision. We allow a total investment of £1.873m, which includes the additional £1.493m which we now pass at final determination. | Response to Ofwat's draft determination on our business plan for 2020 to 2025 | Robustness and efficiency of costs | Fail | The total expenditure assessed within the robustness and efficiency of cost gate is £0.400m which is comprised of the following: - Power resilience and borehole installations (assessment of 'power resilience' component only) £0.400m, fail. Insufficient evidence has been provided to demonstrate that the company's costs are efficient. The company's state that its costs are built up from bottom up quantity surveying rates, scopes of works have been challenged and projected efficiencies applied to scheme costs. (Appendix A29, s3.2.2, p77). The company is claiming that its base costs put it above upper quartile catch up efficiency level and that the company efficiency challenge should be removed (Appendix RA02). There is no evidence on the specific scheme to demonstrate that costs are efficient and for this reason the company efficiency challenge is applied. Our assessment at this gate remains unchanged from the IAP, however we acknowledge that we incorrectly assigned the status of this gate as ‘Partial Pass’ at that time. As ‘network resilience’ has not passed the needs gate, it has not been assessed. The total investment passed within the gate is £0.380m. | Appendix RA02 - Addendum to appendix A29 – wholesale water enhancement cost allowance, April 2019. Appendix A29 Capital investment to deliver a class leading service, Sep 2018 | Robustness and efficiency of costs | Partial pass | The company's state that their costs are built up from bottom up quantity surveying rates, scopes of works have been challenged and projected efficiencies applied to scheme costs. (Appendix A29, s3.2.2, p77). More information could have been provided to evidence this and a company specific efficiency challenge has been applied. | Appendix A29, s3.2.2, p70-77
Customer protection | Pass | We consider the additional allowance made at final determination and determine that it does not require customer protection due to the low materiality of the investment; the assessment from draft determination remains unchanged. | Response to Ofwat's draft determination on our business plan for 2020 to 2025 | Customer protection | Pass | Customer protection is satisfactory. The company includes the range of common resilience and asset health performance commitments designed to incentivise resilience. The company has not proposed a specific performance commitment associated with the delivery of the resilience enhancements scheme, however given the scale and nature of the scheme this is accepted. No further evidence is provided in the April 2019 submission regarding customer protection. |  | Customer protection | Pass | The company includes the range of common resilience and asset health PCs designed to incentivise resilience. The company has not proposed a specific PC associated with the delivery of the resilience enhancements, given the scale and nature of the schemes this is accepted.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A

## Deep dive NWT
FD - Deep dive sheet - United Utilities |  |  |  | DD - Deep dive sheet - United Utilities |  |  |  | IAP - Deep dive sheet - United Utilities
Summary at FD |  |  |  | Summary at DD
Company | NWT |  |  | Company | NWT
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 107.9332 |  |  | Totex carried through deep dive AMP7 (£m) | 107.9332
Totex assessed within cost adjustment claims (£m) | 72.681 | We amend an error in the 'Totex assessed within cost adjustment claims' for draft determinations (£85.681m) to the correct amount, £72.681m. |  | Totex assessed within cost adjustment claims (£m) | 85.681
Totex assessed within deep dive (£m) | 35.2522 |  |  | Totex assessed within deep dive (£m) | 22.2522 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 57.4 |  |  | Totex allowance from cost adjustment claims (£m) | 57.4
Totex allowance from deep dive (£m) | 21.1852 |  |  | Totex allowance from deep dive (£m) | 21.1396 |  |  | Expenditure carried through deep dive AMP7 (£m) | 22.2522
Ofwat view of totex allowance for AMP7 (£m) | 78.5852 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 78.5396 |  |  | Ofwat view of allowance for AMP7 (£m) | 22.2522
`
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | J000 - README - Representations on slow track draft determinations J003 – Cost assessment | Need for investment | Partial pass | Unchanged from IAP |  | Need for investment | Partial pass | The investment requested in this line is a combination of items relating to the Manchester & Pennines resilience scheme and investment related to improving supply interruptions performance in the water network. The majority of the investment relating to the scheme to enhance water supply resilience for customers in Manchester and the Pennines has been assessed under the Cost adjustment Claim process (£72.7m). Investment related to scheme started in AMP6 carrying over into AMP7 on the new tunnel to replace worst condition/highest risk section of tunnel T02 (1.1km) is considered appropriate to this enhancement line (Construction of T02) £22.3m. The installation of pressure surge detection and alleviation, new strategic valves and cross connections and fast-fill network valves (£12.952 m) is regarded as activity funded under base. | S6025_Enhancement_water_network_5, Pages 2 - 8. M&PR need described in The company_WN1_M
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A | NA
Management control | N/A |  |  | Management control | N/A |  |  | Management control | N/A | NA
Best option for customers | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | J000 - README - Representations on slow track draft determinations J003 – Cost assessment | Best option for customers | Pass | As at IAP. No change in our assessment |  | Best option for customers | Pass | T02 Hallbank tunnel project is to replace (using parallel tunnel/pipes) the worst section of the Haweswater Aqueduct (“HA”) which has been identified as requiring urgent rehabilitation. The company reports that work has already started using AMP6 efficiency savings and the AMP7 spend covers completion of the project in 2020-21. The company provides evidence to support replacement as the best option for this length due to its poor condition. This includes results of survey work undertaken during two outages during 2013 and 2016 where the company found significant sections with lining defects, with the Hallbank section identified as the most imminent risk of lining failure. | S6025_Enhancement_water_network_5, Pages 2 - 8. M&PR need described in The company_WN1_M + Other The company_WN1_XX documents
Robustness and efficiency of costs | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | J000 - README - Representations on slow track draft determinations J003 – Cost assessment | Robustness and efficiency of costs | Partial pass | Unchanged from IAP |  | Robustness and efficiency of costs | Partial pass | The company states the costs for the T02 Hallbank tunnel replacement have been derived based on a tendering process. The estimate is therefore a market driven price. However, further evidence to confirm this statement not provided. | S6025_Enhancement_water_network_5, Pages 2 - 8.
Customer protection | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | J000 - README - Representations on slow track draft determinations J003 – Cost assessment | Customer protection | Partial pass | Unchanged from IAP |  | Customer protection | Partial pass | The company states that the replacement of the T02 Hallbank tunnel is subject to a DWI Notice. However, only a DWI letter of support for the M&PR scheme as a whole has been provided. | S6025_Enhancement_water_network_5, Pages 2 - 8.
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A | NA
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A | NA

## Deep Dive SWB
FD - Deep dive sheet - South West Water |  |  |  | DD - Deep dive sheet - South West Water |  |  |  | IAP - Deep dive sheet - South West Water
Summary at FD |  |  |  | Summary at DD
Company | SWB |  |  | Company | SWB
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 54.463 |  |  | Totex carried through deep dive AMP7 (£m) | 54.463
Totex assessed within cost adjustment claims (£m) | 33.2634 |  |  | Totex assessed within cost adjustment claims (£m) | 45.471
Totex assessed within deep dive (£m) | 21.1996 |  |  | Totex assessed within deep dive (£m) | 8.992 |  |  | Summary at IAP
Totex allowance from cost adjustment claims (£m) | 31.6 |  |  | Totex allowance from cost adjustment claims (£m) | 26.6107
Totex allowance from deep dive (£m) | 7.1726 |  |  | Totex allowance from deep dive (£m) | 6.8339 |  |  | Expenditure carried through deep dive AMP7 (£m) | 8.991
Ofwat view of totex allowance for AMP7 (£m) | 38.7726 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 33.4446 |  |  | Ofwat view of allowance for AMP7 (£m) | 7.1928
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | The company has accepted our draft determination for most investments. However, it has made representations for the following investment: • Resilient Service Improvement (£9.962m): The company provides evidence on the activities associated with the investment, which intends to demonstrate that these are, in fact, enhancement activities. However, the specific activities outlined in the evidence involve, according to the company: “physical assets and telemetry for deployment on the network, programme management, new infrastructure to accommodate the incident room and data centre make up the non-IS investment. IS related expenditure comprises new software and systems to provide the information and data to the data centre for analysis and central decision making.” We consider all of these related to base cost activities, such as incident management, equipment replacement (e.g. software and telemetry), and other day-to-day control and management systems. As a consequence, we do not pass the investment within this gate. In addition, we assess opex (£1.800m) that has been excluded at draft determination. The company states that "additional opex of £1.800m over 2020-25 are required to maintain new assets installed at four sites, cyber improvements in control system networks at water works and network enhancements to reduce customer single source exposure." The investment aims at maintaining infrastructure and relates to regular running costs that should be covered by base funding. Further, the company does not specify the maintenance activities that will require funding for each new asset. The total value of the investment that we accept within the need gate for final determinations is £9.437. | Securing Cost Efficiency - supporting information final SWB_Table and model commentaries_FINAL | Need for investment | Partial pass | Unchanged from IAP |  | Need for investment | Partial pass | The investment related to the prevention of flooding at four sites (£4.125m) is appropriate to include within this investment line. Further we considered that the investment related to Cyber improvements in Operational Technology (OT) control system networks at water treatment works, and network enhancements to reduce customer single source exposure (£5.781) could be considered as resilience or Non-SEMD related security enhancement and costs have been allocated accordingly. We have allocated a proportion of the investment from the management and general freeform line (£2.09m) to this area. The investment related to Knapp Mill and Alderney WTWs has been assessed under the cost adjustment claim process (£33.3M). Further we consider that the investment allocated to this line relating to the PUROS and iOPS opex reduction, and RSI (Resilience and Service Improvement) (£9.96m) would be best assessed as base expenditure as it appears to relate to updating IT control systems. | SWB_Table and model commentaries_FINAL, pages: PUROS, etc., = 268, M&G = p267, Line 14 resilience = p265
Need for adjustment | N/A |  |  | Need for adjustment | N/A | NA |  | Need for adjustment | N/A | NA
Management control | N/A |  |  | Management control | N/A | NA |  | Management control | N/A | NA
Best option for customers | Fail | The company has not raised substantive issues in its representation and we retain our draft determination 20% optioneering challenge. | Securing Cost Efficiency - supporting information final SWB_Table and model commentaries_FINAL | Best option for customers | Fail | We have not identified any new evidence and retain our assessment from IAP |  | Best option for customers | Fail | The company provided no evidence to demonstrate any other options have been assessed. Due to the lack of evidence of an appropriate level of optioneering to identify the best value option for customers a 20% efficiency challenge has been applied to the schemes passing the needs gate. | NA
Robustness and efficiency of costs | Fail | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | Securing Cost Efficiency - supporting information final SWB_Table and model commentaries_FINAL | Robustness and efficiency of costs | Fail | We have not identified any new evidence and retain our assessment from IAP |  | Robustness and efficiency of costs | Fail | The company provided no evidence to demonstrate cost build up and efficiency apart from assurance of SWB's costing approach and cost base in general. | NA
Customer protection | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | Securing Cost Efficiency - supporting information final SWB_Table and model commentaries_FINAL | Customer protection | Pass | As at IAP. No change in our assessment |  | Customer protection | Pass | The company has proposed the common resilience PCs and a bespoke PC for water resilience which includes a financial incentive related to the number of customers that experience a loss of mains supply for >12hrs.
Affordability | N/A |  |  | Affordability | N/A | NA |  | Affordability | N/A | NA
Board assurance | N/A |  |  | Board assurance | N/A | NA |  | Board assurance | N/A | NA

## Deep Dive SVE
FD - Deep dive sheet - Severn Trent Water |  |  |  | DD - Deep dive sheet - Severn Trent Water |  |  |  | IAP - Deep dive sheet - Severn Trent Water
Summary at FD |  |  |  | Summary at DD
Company | SVE |  |  | Company | SVE
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 137.001 |  |  | Totex carried through deep dive AMP7 (£m) | 137.001
Totex assessed within cost adjustment claims (£m) | 0 |  |  | Totex assessed within cost adjustment claims (£m) | 0 |  |  | Summary at IAP
Totex assessed within deep dive (£m) | 137.001 |  |  | Totex assessed within deep dive (£m) | 137.001
Totex allowance from cost adjustment claims (£m) | 0 |  |  | Totex allowance from cost adjustment claims (£m) | 0
Totex allowance from deep dive (£m) | 107.15 |  |  | Totex allowance from deep dive (£m) | 107.15 |  |  | Expenditure carried through deep dive AMP7 (£m) | 135.396
Ofwat view of totex allowance for AMP7 (£m) | 107.15 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 107.15 |  |  | Ofwat view of allowance for AMP7 (£m) | 107.15
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | Partial pass | To reflect our move from a capex to a totex approach, we assess an additional £1.605m of opex related to the Birmingham Resilience scheme (2015-2020 scheme, becoming operational in 2019/20). The expenditure is linked to the £12.000m opex of the Birmingham Resilience scheme after the opex from the period 2015-2020 has been removed. This expenditure involves maintenance of the new infrastructure asset, for which the company receives a base allowance, and is therefore not accepted as a resilience enhancement. The total value of the investment that we accept within the need gate for final determinations remains as per our draft determination. | 1. Cover letter sve_appendix_a8_securing_cost_efficiency | Need for investment | Pass | Unchanged from IAP |  | Need for investment | Pass | The company presents clear plans to improve the resilience of its strategic grid network, focusing on the following areas: strategic supply assets & trunk mains, large surface water treatment works and groundwater works and network assets. Lessons learnt from the Mythe incident in 2007 and the recent work on the Birmingham resilience scheme, as well as information gained from the Elan Valley Aqueduct and United Utilities’ Haweswater Aqueduct have been reviewed in developing the business case. The expenditure can be summarised into the following sub-investments: Strategic Supply Assets (£29m) & Trunk Mains (£10m), Large Surface Water Treatment Works (£54m) & Groundwater Sites (£14m) and Network response to a treatment work failure (£21m) & Distribution Resilience (£7m). Resilience expenditure is expected to be related to low probability-high consequence events that would not normally be evident in historical levels of service (due to their low frequency of occurrence). In the absence of this and regulatory drivers the clear support of customers is expected. The strategic supply asset investment relates to single points of failure on the trunk main network including the strategic link from Bamford to Ambergate. The company states that "...These assets are complex in their operation and unique in their construction... and therefore present a single point of failure...(Appendix 8, p268)" with the potential to impact large numbers of customer. This is consistent with our definition of this investment area as it relates to resolving risks of a single source of supply. Further the trunk main risk assessments relate to "...principally reviewing the risk of structural failure, failure caused by natural hazard or failure caused by 3rd party." (Appendix 8, p62). These are a low probability, high magnitude events. Duration assessments and alternative approaches have been considered and only interventions on trunk mains where a 24hr supply interruption is likely have been included in investment plans, "This has resulted in reducing our list to only 2,699 mains which do not have the capability to avoid an interruption to supply for longer than 24hrs in the event of a failure" (Appendix 8, p262). The company states that "...To help us understand the impact of a failure of our strategic surface water treatment works, we completed a further study in June 2016 to improve our understanding of the capability, capacity and constraints of the Strategic Grid and other assets both today and at the end of AMP6. This involved stress testing our water treatment works’ production capability under a range of scenarios." (Appendix 8, p269). Therefore the impact of losing each of the 4 major WTWs on the strategic grid have been assessed highlighting 4 areas where there were significant properties at risk of supply interruptions and/or discoloured water issues and interventions included in this submission. Relating to the groundwater sites the company states that "...we have reviewed all 108 of our groundwater sites and appraised their vulnerability to long duration interruptions (>24hrs), principally reviewing the risk of aquifer pollution and/or mechanical or electrical failure, power failure and extreme flooding.... We have simulated the impacts of failure and the options we have to provide resilience from elsewhere in our system or elsewhere on the site. This has resulted in our list of sites which do not have the capability to avoid an interruption to supply for longer than 24hrs in the event of a failure. We have assessed if any redundancy or resistance options exist, should exist or have ever existed at these sites. Where they do our sites do not form part of this proposal". The risk identification process has covered extreme events such as flooding and power failure and therefore can be considered to be linked to low probability, high consequence events that are expected in this expenditure line. The company have identified areas of their network where if required to respond to a major treatment works failure and reverse flows they would likely cause discolouration and/or a long term supply interruption. The investment relates to 19 interventions identified to mitigate this risk. However we consider that companies are already funded to maintain their supply network to avoid discolouration. The company further states that for customers, interruptions of longer than 24 hours are not acceptable; prolonged periods of discolouration for some customers are tantamount to a supply interruption; an equivalent minimum level of resilience for all customers should be provided; and interruptions in supply caused by a single point of failure are unacceptable (sve_appendix_a8_securing_cost_efficiency, p55). Under distribution resilience (£7m) the company includes investment for local resilience, pressure transients and enhanced network conditioning. Local resilience schemes are driven by a range of strategic network connections and therefore links directly to improving supply interruptions performance. Such investments are considered to relate to securing routine operations and the need under this expenditure lines is not accepted. | water_forum_report_2018; sve_appendix_a8_securing_cost_efficiency
Need for adjustment | N/A |  |  | Need for adjustment | N/A | NA |  | Need for adjustment | N/A | NA
Management control | N/A |  |  | Management control | N/A | NA |  | Management control | N/A | NA
Best option for customers | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | 1. Cover letter sve_appendix_a8_securing_cost_efficiency | Best option for customers | Partial pass | Unchanged from IAP |  | Best option for customers | Partial pass | The company has provided a reasonable level of detail in their methods and calculations that underpin key elements of the claim relating to the identification and prioritisation of risks (e.g. failure probability derivation, cost calculations, impacts of failure on customer supply, estimation of benefits). However, while the main components of a robust options appraisal process are included in the business case (incorporating customer views into options development & consideration of a full range of resilience options), there is not enough detail to fully verify the appropriateness of the company's preferred option. The company states that its cost adjustment claims have received technical and regulatory assurance from Jacobs, and the specific roles carried out by Jacobs in some of the areas is stated, whereas in this particular area it is not. The options analysis would have been significantly improved by greater evidence of external technical assurance. On this basis adjustments have been made to the requested investment. Specifically for the trunk mains investment there is a benefit to asset health that has not been acknowledged. Further evidence should have been presented on likelihood of failures and therefore it is difficult to ascertain whether the scheme can be considered as the most cost effective or the highest priority area for investment. For large WTW there may be a significant benefit across both local SDB and resilience through the dual streaming of these works. The evidence provided was not considered sufficient to provide confidence that all possible options, including lower scope mitigations for specific points of failures have been rigorously review. Again for Groundwater treatment works investment area there is insufficient evidence presented on likelihood of failures and therefore it is difficult to judge whether the scheme can be considered as the most cost effective or the highest priority area for investment. The adjustments made are summarised in the box below. | sve_appendix_a1_engaging_customers sve_appendix_a8_securing_cost_efficiency sve_appendix_a12_securing_trust_confidence_and_assurance
Robustness and efficiency of costs | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | 1. Cover letter sve_appendix_a8_securing_cost_efficiency | Robustness and efficiency of costs | Partial pass | Unchanged from IAP |  | Robustness and efficiency of costs | Partial pass | The company state that the costs of the projects have been established through 1.) STW cost curves & unit rates established, updated and refined over the last 15yrs for similar activity; 2.) Cost data provided by an independent engineering consultant with specialist cost data sets; and 3.) Best practice guidance on understanding and applying an appropriate level of optimism bias within our projects", p293. This approach appears reasonable and has been assured at different levels, but only high-level costs (CAPEX and annualised OPEX) have been provided for the preferred options. Not all feasible options were provided with the same level of detail; in general, only NPV of benefits minus costs are provided for most options, but this information is only given for the preferred option in the network assets. However, the basis of these costs and their derivation are not explained. There is concern regarding the application of optimism bias to these types of investment. In addition the company also states they "have then tested the efficiency of these [estimating approaches] using an independent expert (Turner & Townsend) by; 1.) Benchmark testing a selection of representative projects; and 2.) Benchmark testing a number of programme level costs e.g. feasibility fee, design fee, project support costs." Further cost efficiency benchmarking is set against the background of having secured programme optimisation and project optimisation savings such that they accrue in their entirety to customers. On this programme of work we estimate that these costs are in excess of £100m capex.", p293. On this basis and the previous conclusions regarding the justification of the preferred option a 20% adjustment has been applied to all investments for which the need was accepted. The investment for strategic supply assets has been allowable in full. | sve_appendix_a8_securing_cost_efficiency
Customer protection | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. | 1. Cover letter sve_appendix_a8_securing_cost_efficiency | Customer protection | Pass | As at IAP. No change in our assessment |  | Customer protection | Pass | The company proposes a new PC with an end of period ODI for resilience that covers both source and network resilience under normal conditions (peak demand, multiple failure scenarios and drought conditions are outside of the PC) p294. | sve_appendix_a8_securing_cost_efficiency
Affordability | N/A |  |  | Affordability | N/A | NA |  | Affordability | N/A | NA | sve_appendix_a8_securing_cost_efficiency
Board assurance | N/A |  |  | Board assurance | N/A | NA |  | Board assurance | N/A | NA | sve_appendix_a8_securing_cost_efficiency
Further analysis / arguments
In conclusion the investment is generally in line with our expectation in terms of resilience expenditure. It is relatively well defined, is related to a performance commitment and has customer support. However there are elements of this plan that we consider to be funded under the day-to-day operations and this investment has not been allowed as the case has not made as to the need. Further the company did not fully evidence how they determined their preferred options in many circumstances. The following adjustments were made:
Requested Allowed
Strategic Supply Assets £29m £29m
Trunk Mains £10m £8m
Large Surface Water Treatment Works £54m £43.20m
Groundwater Sites £14m £11.20m
Network response to a treatment work failure £21m £15.75m
Distribution Resilience £7m £0m