## Cover
Cover sheet
Taste, odour and colour enhancement feeder model
Objective
To assess enhancement total expenditure (totex) included by companies in their PR19 business plan submissions in the pre-defined lines in Table WS2 for 'Improving taste / odour / colour'.
Approach
We assess the investment for these lines based on the materiality of the expenditure requested, after any cost reallocations. As no suitable cost drivers could be identified for econometric modelling we deep dive the five companies for which the proposed investment is material and shallow dive the remaining two. In our assessment we look for evidence of Drinking Water Inspectorate support for schemes and the size of the works involved to quantify the scale of the enhancements. We apply our company-specific efficiency challenge to any costs that we shallow dive. For the deep dive assessments, we consider the availability and quality of evidence provided. Note: The materiality of the requested expenditure is assessed by reference to the total 2020-25 totex for the water service as indicated in Table WS1 of companies' September 2018 / April 2019 business plans and not any more recent update.
Principal changes at draft determinations
We moved from a capex approach to a totex approach for slow track and significant scrutiny companies at draft determinations. For consistency, we are now including an opex allowance for fast track companies in order to have a totex allowance for all companies at final determinations.
The diagram above is a simplified process model to indicate the relationship between the various feeder models and data sources we use to assess wholesale and retail expenditure cost efficiency models. We provide a detailed process map in ‘PR19 price setting models map - slow track draft determinations’.
Model presented in the current file
Key:
FM = Feeder model
CAC = Cost adjustment claim
CPIH = Consumer Prices Index including owner occupiers’ housing costs
ONS = Office for National Statistics
MHCLG = Ministry of Housing, Communities and Local Government
HVT = Havant Thicket
TTT = Thames Tideway

## F_inputs
FM_E_WW_tasteodourcolour
Acronym | Reference | Item description | Unit | Model | Description_input | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2020-25
ANH | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0.23471 | 0.015557 | 0.0016389 | -0.0046807 | 0.0048399 | 0 | 0 | 0 | 0 | 0 | 0
ANH | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 369.5998 | 393.9067 | 354.537 | 370.2469 | 327.6219 | 375.7071 | 399.9078 | 442.6981 | 397.8529 | 494.8537 | 569.1626 | 614.4832 | 601.174 | 466.5721
ANH | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
ANH | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
ANH | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
WSH | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2.9008 | 0.88265 | 1.67 | 3.8959 | 4.3386 | 1.3096 | 7.664 | 10.8012 | 7.4638 | 8.066 | 7.656 | 6.171 | 2.653 | 2.633
WSH | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 273.9076 | 296.8508 | 299.6694 | 330.2704 | 238.9135 | 320.2603 | 354.3857 | 342.0294 | 300.7342 | 338.873 | 347.164 | 338.818 | 324.732 | 316.383
WSH | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0.05; 2018-19: 0.05; 2019-20: 0.05; 2020-21: 0.008; 2021-22: 0.008; 2022-23: 0.008; 2023-24: 0.008; 2024-25: 0.008
WSH | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
WSH | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
HDD | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0.53196; 2023-24: 0.53196; 2024-25: 0.53196
HDD | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 2017-18: 28.8835; 2018-19: 31.6394; 2019-20: 24.7939; 2020-21: 27.46; 2021-22: 27.121; 2022-23: 26.327; 2023-24: 25.742; 2024-25: 26.044
HDD | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0.036411; 2021-22: 0.056411; 2022-23: 0.041411; 2023-24: 0.041411; 2024-25: 0.041411
HDD | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
HDD | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
NES | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2.1162 | -0.035608 | -0.0042279 | 0 | 0.07179 | 3.7492 | 5.544 | 2.5245 | 0.31414 | 0 | 0 | 0 | 0 | 0
NES | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 334.7369 | 301.2122 | 287.3082 | 277.2513 | 291.5084 | 284.6257 | 344.341 | 367.7514 | 334.5254 | 348.078 | 368.717 | 360.499 | 337.229 | 311.733
NES | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0.078; 2018-19: 0; 2019-20: 0.061; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
NES | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
NES | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
SVE | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2017-18: 3.812; 2018-19: 0.050059; 2019-20: -0.11395; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
SVE | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 2017-18: 687.9725; 2018-19: 757.2387; 2019-20: 799.0685; 2020-21: 575.0657; 2021-22: 631.1286; 2022-23: 643.4347; 2023-24: 635.4116; 2024-25: 630.7635
SVE | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 2.1604; 2018-19: 2.2339; 2019-20: 2.3022; 2020-21: 4.1456; 2021-22: 4.1502; 2022-23: 4.2291; 2023-24: 4.704; 2024-25: 5.2157
SVE | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
SVE | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
SVT | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2011-12: 0.13022; 2012-13: -0.012948; 2013-14: 0.54818; 2014-15: 3.4035; 2015-16: 7.2752; 2016-17: 1.2399; 2017-18: 1.111
SVT | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 2011-12: 518.0027; 2012-13: 557.0869; 2013-14: 583.1486; 2014-15: 611.9245; 2015-16: 587.1872; 2016-17: 609.9451; 2017-18: 683.786
SVT | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
SVT | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019
SVT | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019
SWB | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56
SWB | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 168.5464 | 139.5375 | 159.757 | 158.564 | 154.9662 | 171.9259 | 175.102 | 146.7962 | 138.7275 | 164.926 | 179.669 | 192.194 | 181.702 | 175.761
SWB | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
SWB | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
SWB | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
SWT | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2011-12: 0; 2012-13: 0; 2013-14: 0; 2014-15: 0; 2015-16: 0
SWT | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 2011-12: 140.7011; 2012-13: 113.3753; 2013-14: 129.4919; 2014-15: 130.1755; 2015-16: 128.9304
SWT | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
SWT | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019
SWT | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019
SRN | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | -0.0022101 | 0.025897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SRN | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 208.0852 | 162.4407 | 158.0999 | 150.6366 | 132.0083 | 165.5298 | 227.072 | 212.6489 | 211.2972 | 238.969 | 240.008 | 219.66 | 201.802 | 217.626
SRN | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
SRN | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
SRN | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
TMS | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TMS | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 655.6572 | 618.3888 | 634.9723 | 682.7605 | 747.529 | 849.161 | 895.282 | 960.4243 | 1024.5945 | 1009.8378 | 1101.9036 | 1077.4233 | 1033.9695 | 997.9188
TMS | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
TMS | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
TMS | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
NWT | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 33.1847 | 34.8986 | 21.5808 | 13.4925 | 0.85435 | 0.51343 | 1.1735 | 4.2692 | 0.057749 | 1.3802 | 1.8995 | 4.0644 | 1.3693 | 1.3033
NWT | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 531.2972 | 554.3658 | 550.9866 | 545.1088 | 549.5249 | 612.8371 | 601.4976 | 621.8529 | 528.1722 | 546.9142 | 511.026 | 491.8832 | 466.2618 | 461.4183
NWT | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0.3633; 2021-22: 0.3657; 2022-23: 0.36753; 2023-24: 0.3688; 2024-25: 0.37008
NWT | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
NWT | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
WSX | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2.2256 | 6.2357 | 2.8189 | 0.76706 | 0.13096 | 1.0007 | 1.7063 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSX | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 160.1115 | 176.2073 | 161.725 | 155.7696 | 161.7977 | 157.5438 | 135.1825 | 135.5478 | 145.6387 | 134.2655 | 125.5988 | 144.2895 | 125.3448 | 120.5543
WSX | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: -0.038669; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
WSX | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
WSX | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
YKY | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.75 | 4.437 | 3.45 | 2.276 | 1.901
YKY | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 390.8034 | 309.4734 | 263.5993 | 271.3183 | 295.5084 | 337.3085 | 369.595 | 414.498 | 394.0111 | 385.797 | 385.065 | 393.66 | 376.679 | 345.664
YKY | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0.193
YKY | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
YKY | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
AFW | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 1.7927 | 3.2648 | 0.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AFW | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 212.9247 | 219.3039 | 224.1049 | 216.4519 | 237.3466 | 275.8073 | 255.5782 | 240.0907 | 226.3173 | 287.61 | 290.6915 | 281.3912 | 264.4597 | 241.8721
AFW | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
AFW | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
AFW | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
BWH | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BWH | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 27.8454 | 26.1622 | 30.2651 | 28.3885 | 26.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BWH | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
BWH | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019
BWH | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019
BRL | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BRL | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 106.8552 | 136.6866 | 124.5262 | 111.4734 | 74.0819 | 85.1219 | 103.363 | 104.8207 | 101.8476 | 91.388 | 89.27 | 89.474 | 89.114 | 89.552
BRL | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
BRL | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
BRL | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
DVW | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 2011-12: 0; 2012-13: 0; 2013-14: 0; 2014-15: 0; 2015-16: 0.13557; 2016-17: 1.3626; 2017-18: 2.713
DVW | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 2011-12: 18.4007; 2012-13: 24.2402; 2013-14: 15.9632; 2014-15: 17.1151; 2015-16: 16.9084; 2016-17: 22.0046; 2017-18: 27.924
DVW | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
DVW | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019
DVW | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019
PRT | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0.011051 | 0.0053952 | 0.0042279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRT | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 28.1062 | 32.8684 | 27.5265 | 27.2787 | 28.6556 | 32.4848 | 27.996 | 36.0049 | 35.8795 | 45.14 | 38.365 | 39.048 | 51.654 | 53.923
PRT | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
PRT | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
PRT | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
SEW | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0.11549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEW | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 158.0452 | 166.4331 | 171.0139 | 167.4904 | 161.5074 | 162.5752 | 171.97 | 180.8624 | 169.0072 | 172.073 | 199.614 | 208.204 | 186.195 | 194.588
SEW | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
SEW | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
SEW | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0
SSC | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7288 | 22.7288 | 23.7464 | 1.0177 | 1.0177
SSC | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 79.0064 | 86.0693 | 80.0066 | 80.0541 | 83.4035 | 87.873 | 95.2708 | 91.7522 | 91.6349 | 113.2581 | 115.4825 | 116.3865 | 93.9133 | 96.8046
SSC | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 1.0793; 2023-24: 1.0327; 2024-25: 0.99775
SSC | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
SSC | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 68.023
SES | C_W3003CAW_PR19CA001 | Total wholesale water - Improving taste / odour / colour | £m | Price Review 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SES | C_W3026TECAW_PR19CA001 | Total wholesale water - Total expenditure | £m | Price Review 2019 |  | 52.1689 | 46.4448 | 48.576 | 46.034 | 44.7511 | 49.3363 | 51.205 | 52.3625 | 53.7106 | 52.777 | 57.544 | 52.131 | 46.371 | 45.346
SES | WS2013CAW | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | £m | Price Review 2019 |  | 2017-18: 0; 2018-19: 0; 2019-20: 0; 2020-21: 0; 2021-22: 0; 2022-23: 0; 2023-24: 0; 2024-25: 0
SES | C_W3003CAC_PR19WR | Total CAC-WW_Improving taste / odour / colour-WR | £m | Price Review 2019 |  | 2020-25: 0
SES | C_W3003CAC_PR19WN | Total CAC-WW_Improving taste / odour / colour-WN | £m | Price Review 2019 |  | 2020-25: 0

## Data
Data
£m 2017-18 prices
|  |  | C_W3003CAW_PR19CA001 | C_W3026TECAW_PR19CA001 | WS2013CAW
Code | Company | Year | £m, Enhancement capex water - Improving taste / odour / colour | £m 2017-18 prices, Totex wholesale water (including cash items and atypical expenditure) | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total
ANH12 | ANH | 2011-12 | 0 | 369.5998 | 0
ANH13 | ANH | 2012-13 | 0 | 393.9067 | 0
ANH14 | ANH | 2013-14 | 0 | 354.537 | 0
ANH15 | ANH | 2014-15 | 0.23471 | 370.2469 | 0
ANH16 | ANH | 2015-16 | 0.015557 | 327.6219 | 0
ANH17 | ANH | 2016-17 | 0.0016389 | 375.7071 | 0
ANH18 | ANH | 2017-18 | -0.0046807 | 399.9078 | 0
ANH19 | ANH | 2018-19 | 0.0048399 | 442.6981 | 0
ANH20 | ANH | 2019-20 | 0 | 397.8529 | 0
ANH21 | ANH | 2020-21 | 0 | 494.8537 | 0
ANH22 | ANH | 2021-22 | 0 | 569.1626 | 0
ANH23 | ANH | 2022-23 | 0 | 614.4832 | 0
ANH24 | ANH | 2023-24 | 0 | 601.174 | 0
ANH25 | ANH | 2024-25 | 0 | 466.5721 | 0
NES12 | NES | 2011-12 | 2.1162 | 334.7369 | 0
NES13 | NES | 2012-13 | -0.035608 | 301.2122 | 0
NES14 | NES | 2013-14 | -0.0042279 | 287.3082 | 0
NES15 | NES | 2014-15 | 0 | 277.2513 | 0
NES16 | NES | 2015-16 | 0.07179 | 291.5084 | 0
NES17 | NES | 2016-17 | 3.7492 | 284.6257 | 0
NES18 | NES | 2017-18 | 5.544 | 344.341 | 0.078
NES19 | NES | 2018-19 | 2.5245 | 367.7514 | 0
NES20 | NES | 2019-20 | 0.31414 | 334.5254 | 0.061
NES21 | NES | 2020-21 | 0 | 348.078 | 0
NES22 | NES | 2021-22 | 0 | 368.717 | 0
NES23 | NES | 2022-23 | 0 | 360.499 | 0
NES24 | NES | 2023-24 | 0 | 337.229 | 0
NES25 | NES | 2024-25 | 0 | 311.733 | 0
NWT12 | NWT | 2011-12 | 33.1847 | 531.2972 | 0
NWT13 | NWT | 2012-13 | 34.8986 | 554.3658 | 0
NWT14 | NWT | 2013-14 | 21.5808 | 550.9866 | 0
NWT15 | NWT | 2014-15 | 13.4925 | 545.1088 | 0
NWT16 | NWT | 2015-16 | 0.85435 | 549.5249 | 0
NWT17 | NWT | 2016-17 | 0.51343 | 612.8371 | 0
NWT18 | NWT | 2017-18 | 1.1735 | 601.4976 | 0
NWT19 | NWT | 2018-19 | 4.2692 | 621.8529 | 0
NWT20 | NWT | 2019-20 | 0.057749 | 528.1722 | 0
NWT21 | NWT | 2020-21 | 1.3802 | 546.9142 | 0.3633
NWT22 | NWT | 2021-22 | 1.8995 | 511.026 | 0.3657
NWT23 | NWT | 2022-23 | 4.0644 | 491.8832 | 0.36753
NWT24 | NWT | 2023-24 | 1.3693 | 466.2618 | 0.3688
NWT25 | NWT | 2024-25 | 1.3033 | 461.4183 | 0.37008
SRN12 | SRN | 2011-12 | -0.0022101 | 208.0852 | 0
SRN13 | SRN | 2012-13 | 0.025897 | 162.4407 | 0
SRN14 | SRN | 2013-14 | 0 | 158.0999 | 0
SRN15 | SRN | 2014-15 | 0 | 150.6366 | 0
SRN16 | SRN | 2015-16 | 0 | 132.0083 | 0
SRN17 | SRN | 2016-17 | 0 | 165.5298 | 0
SRN18 | SRN | 2017-18 | 0 | 227.072 | 0
SRN19 | SRN | 2018-19 | 0 | 212.6489 | 0
SRN20 | SRN | 2019-20 | 0 | 211.2972 | 0
SRN21 | SRN | 2020-21 | 0 | 238.969 | 0
SRN22 | SRN | 2021-22 | 0 | 240.008 | 0
SRN23 | SRN | 2022-23 | 0 | 219.66 | 0
SRN24 | SRN | 2023-24 | 0 | 201.802 | 0
SRN25 | SRN | 2024-25 | 0 | 217.626 | 0
SVT12 | SVT | 2011-12 | 0.13022 | 518.0027 | 0
SVT13 | SVT | 2012-13 | -0.012948 | 557.0869 | 0
SVT14 | SVT | 2013-14 | 0.54818 | 583.1486 | 0
SVT15 | SVT | 2014-15 | 3.4035 | 611.9245 | 0
SVT16 | SVT | 2015-16 | 7.2752 | 587.1872 | 0
SVT17 | SVT | 2016-17 | 1.2399 | 609.9451 | 0
SVT18 | SVT | 2017-18 | 1.111 | 683.786 | 0
SVT19 | SVT | 2018-19 | 0 | 0 | 0
SVT20 | SVT | 2019-20 | 0 | 0 | 0
SVT21 | SVT | 2020-21 | 0 | 0 | 0
SVT22 | SVT | 2021-22 | 0 | 0 | 0
SVT23 | SVT | 2022-23 | 0 | 0 | 0
SVT24 | SVT | 2023-24 | 0 | 0 | 0
SVT25 | SVT | 2024-25 | 0 | 0 | 0
SWT12 | SWT | 2011-12 | 0 | 140.7011 | 0
SWT13 | SWT | 2012-13 | 0 | 113.3753 | 0
SWT14 | SWT | 2013-14 | 0 | 129.4919 | 0
SWT15 | SWT | 2014-15 | 0 | 130.1755 | 0
SWT16 | SWT | 2015-16 | 0 | 128.9304 | 0
SWT17 | SWT | 2016-17 | 0 | 0 | 0
SWT18 | SWT | 2017-18 | 0 | 0 | 0
SWT19 | SWT | 2018-19 | 0 | 0 | 0
SWT20 | SWT | 2019-20 | 0 | 0 | 0
SWT21 | SWT | 2020-21 | 0 | 0 | 0
SWT22 | SWT | 2021-22 | 0 | 0 | 0
SWT23 | SWT | 2022-23 | 0 | 0 | 0
SWT24 | SWT | 2023-24 | 0 | 0 | 0
SWT25 | SWT | 2024-25 | 0 | 0 | 0
SWB17 | SWB | 2016-17 | 0 | 171.9259 | 0
SWB18 | SWB | 2017-18 | 0 | 175.102 | 0
SWB19 | SWB | 2018-19 | 0 | 146.7962 | 0
SWB20 | SWB | 2019-20 | 0 | 138.7275 | 0
SWB21 | SWB | 2020-21 | 1.56 | 164.926 | 0
SWB22 | SWB | 2021-22 | 1.56 | 179.669 | 0
SWB23 | SWB | 2022-23 | 1.56 | 192.194 | 0
SWB24 | SWB | 2023-24 | 1.56 | 181.702 | 0
SWB25 | SWB | 2024-25 | 1.56 | 175.761 | 0
TMS12 | TMS | 2011-12 | 0 | 655.6572 | 0
TMS13 | TMS | 2012-13 | 0 | 618.3888 | 0
TMS14 | TMS | 2013-14 | 0 | 634.9723 | 0
TMS15 | TMS | 2014-15 | 0 | 682.7605 | 0
TMS16 | TMS | 2015-16 | 0 | 747.529 | 0
TMS17 | TMS | 2016-17 | 0 | 849.161 | 0
TMS18 | TMS | 2017-18 | 0 | 895.282 | 0
TMS19 | TMS | 2018-19 | 0 | 960.4243 | 0
TMS20 | TMS | 2019-20 | 0 | 1024.5945 | 0
TMS21 | TMS | 2020-21 | 0 | 1009.8378 | 0
TMS22 | TMS | 2021-22 | 0 | 1101.9036 | 0
TMS23 | TMS | 2022-23 | 0 | 1077.4233 | 0
TMS24 | TMS | 2023-24 | 0 | 1033.9695 | 0
TMS25 | TMS | 2024-25 | 0 | 997.9188 | 0
WSH12 | WSH | 2011-12 | 2.9008 | 273.9076 | 0
WSH13 | WSH | 2012-13 | 0.88265 | 296.8508 | 0
WSH14 | WSH | 2013-14 | 1.67 | 299.6694 | 0
WSH15 | WSH | 2014-15 | 3.8959 | 330.2704 | 0
WSH16 | WSH | 2015-16 | 4.3386 | 238.9135 | 0
WSH17 | WSH | 2016-17 | 1.3096 | 320.2603 | 0
WSH18 | WSH | 2017-18 | 7.664 | 354.3857 | 0.05
WSH19 | WSH | 2018-19 | 10.8012 | 342.0294 | 0.05
WSH20 | WSH | 2019-20 | 7.4638 | 300.7342 | 0.05
WSH21 | WSH | 2020-21 | 8.066 | 338.873 | 0.008
WSH22 | WSH | 2021-22 | 7.656 | 347.164 | 0.008
WSH23 | WSH | 2022-23 | 6.171 | 338.818 | 0.008
WSH24 | WSH | 2023-24 | 2.653 | 324.732 | 0.008
WSH25 | WSH | 2024-25 | 2.633 | 316.383 | 0.008 | 27.179 | 1665.97 | 0.04
WSX12 | WSX | 2011-12 | 2.2256 | 160.1115 | 0
WSX13 | WSX | 2012-13 | 6.2357 | 176.2073 | 0
WSX14 | WSX | 2013-14 | 2.8189 | 161.725 | 0
WSX15 | WSX | 2014-15 | 0.76706 | 155.7696 | 0
WSX16 | WSX | 2015-16 | 0.13096 | 161.7977 | 0
WSX17 | WSX | 2016-17 | 1.0007 | 157.5438 | 0
WSX18 | WSX | 2017-18 | 1.7063 | 135.1825 | 0
WSX19 | WSX | 2018-19 | 0 | 135.5478 | -0.038669
WSX20 | WSX | 2019-20 | 0 | 145.6387 | 0
WSX21 | WSX | 2020-21 | 0 | 134.2655 | 0
WSX22 | WSX | 2021-22 | 0 | 125.5988 | 0
WSX23 | WSX | 2022-23 | 0 | 144.2895 | 0
WSX24 | WSX | 2023-24 | 0 | 125.3448 | 0
WSX25 | WSX | 2024-25 | 0 | 120.5543 | 0
YKY12 | YKY | 2011-12 | 0 | 390.8034 | 0
YKY13 | YKY | 2012-13 | 0 | 309.4734 | 0
YKY14 | YKY | 2013-14 | 0 | 263.5993 | 0
YKY15 | YKY | 2014-15 | 0 | 271.3183 | 0
YKY16 | YKY | 2015-16 | 0 | 295.5084 | 0
YKY17 | YKY | 2016-17 | 0 | 337.3085 | 0
YKY18 | YKY | 2017-18 | 0 | 369.595 | 0
YKY19 | YKY | 2018-19 | 0 | 414.498 | 0
YKY20 | YKY | 2019-20 | 0 | 394.0111 | 0
YKY21 | YKY | 2020-21 | 4.75 | 385.797 | 0
YKY22 | YKY | 2021-22 | 4.437 | 385.065 | 0
YKY23 | YKY | 2022-23 | 3.45 | 393.66 | 0
YKY24 | YKY | 2023-24 | 2.276 | 376.679 | 0
YKY25 | YKY | 2024-25 | 1.901 | 345.664 | 0.193
AFW12 | AFW | 2011-12 | 0 | 212.9247 | 0
AFW13 | AFW | 2012-13 | 0 | 219.3039 | 0
AFW14 | AFW | 2013-14 | 0 | 224.1049 | 0
AFW15 | AFW | 2014-15 | 0 | 216.4519 | 0
AFW16 | AFW | 2015-16 | 1.7927 | 237.3466 | 0
AFW17 | AFW | 2016-17 | 3.2648 | 275.8073 | 0
AFW18 | AFW | 2017-18 | 0.613 | 255.5782 | 0
AFW19 | AFW | 2018-19 | 0 | 240.0907 | 0
AFW20 | AFW | 2019-20 | 0 | 226.3173 | 0
AFW21 | AFW | 2020-21 | 0 | 287.61 | 0
AFW22 | AFW | 2021-22 | 0 | 290.6915 | 0
AFW23 | AFW | 2022-23 | 0 | 281.3912 | 0
AFW24 | AFW | 2023-24 | 0 | 264.4597 | 0
AFW25 | AFW | 2024-25 | 0 | 241.8721 | 0
BRL12 | BRL | 2011-12 | 0 | 106.8552 | 0
BRL13 | BRL | 2012-13 | 0 | 136.6866 | 0
BRL14 | BRL | 2013-14 | 0 | 124.5262 | 0
BRL15 | BRL | 2014-15 | 0 | 111.4734 | 0
BRL16 | BRL | 2015-16 | 0 | 74.0819 | 0
BRL17 | BRL | 2016-17 | 0 | 85.1219 | 0
BRL18 | BRL | 2017-18 | 0 | 103.363 | 0
BRL19 | BRL | 2018-19 | 0 | 104.8207 | 0
BRL20 | BRL | 2019-20 | 0 | 101.8476 | 0
BRL21 | BRL | 2020-21 | 0 | 91.388 | 0
BRL22 | BRL | 2021-22 | 0 | 89.27 | 0
BRL23 | BRL | 2022-23 | 0 | 89.474 | 0
BRL24 | BRL | 2023-24 | 0 | 89.114 | 0
BRL25 | BRL | 2024-25 | 0 | 89.552 | 0
BWH12 | BWH | 2011-12 | 0 | 27.8454 | 0
BWH13 | BWH | 2012-13 | 0 | 26.1622 | 0
BWH14 | BWH | 2013-14 | 0 | 30.2651 | 0
BWH15 | BWH | 2014-15 | 0 | 28.3885 | 0
BWH16 | BWH | 2015-16 | 0 | 26.0358 | 0
BWH17 | BWH | 2016-17 | 0 | 0 | 0
BWH18 | BWH | 2017-18 | 0 | 0 | 0
BWH19 | BWH | 2018-19 | 0 | 0 | 0
BWH20 | BWH | 2019-20 | 0 | 0 | 0
BWH21 | BWH | 2020-21 | 0 | 0 | 0
BWH22 | BWH | 2021-22 | 0 | 0 | 0
BWH23 | BWH | 2022-23 | 0 | 0 | 0
BWH24 | BWH | 2023-24 | 0 | 0 | 0
BWH25 | BWH | 2024-25 | 0 | 0 | 0
DVW12 | DVW | 2011-12 | 0 | 18.4007 | 0
DVW13 | DVW | 2012-13 | 0 | 24.2402 | 0
DVW14 | DVW | 2013-14 | 0 | 15.9632 | 0
DVW15 | DVW | 2014-15 | 0 | 17.1151 | 0
DVW16 | DVW | 2015-16 | 0.13557 | 16.9084 | 0
DVW17 | DVW | 2016-17 | 1.3626 | 22.0046 | 0
DVW18 | DVW | 2017-18 | 2.713 | 27.924 | 0
DVW19 | DVW | 2018-19 | 0 | 0 | 0
DVW20 | DVW | 2019-20 | 0 | 0 | 0
DVW21 | DVW | 2020-21 | 0 | 0 | 0
DVW22 | DVW | 2021-22 | 0 | 0 | 0
DVW23 | DVW | 2022-23 | 0 | 0 | 0
DVW24 | DVW | 2023-24 | 0 | 0 | 0
DVW25 | DVW | 2024-25 | 0 | 0 | 0
PRT12 | PRT | 2011-12 | 0.011051 | 28.1062 | 0
PRT13 | PRT | 2012-13 | 0.0053952 | 32.8684 | 0
PRT14 | PRT | 2013-14 | 0.0042279 | 27.5265 | 0
PRT15 | PRT | 2014-15 | 0 | 27.2787 | 0
PRT16 | PRT | 2015-16 | 0 | 28.6556 | 0
PRT17 | PRT | 2016-17 | 0 | 32.4848 | 0
PRT18 | PRT | 2017-18 | 0 | 27.996 | 0
PRT19 | PRT | 2018-19 | 0 | 36.0049 | 0
PRT20 | PRT | 2019-20 | 0 | 35.8795 | 0
PRT21 | PRT | 2020-21 | 0 | 45.14 | 0
PRT22 | PRT | 2021-22 | 0 | 38.365 | 0
PRT23 | PRT | 2022-23 | 0 | 39.048 | 0
PRT24 | PRT | 2023-24 | 0 | 51.654 | 0
PRT25 | PRT | 2024-25 | 0 | 53.923 | 0
SES12 | SES | 2011-12 | 0 | 52.1689 | 0
SES13 | SES | 2012-13 | 0 | 46.4448 | 0
SES14 | SES | 2013-14 | 0 | 48.576 | 0
SES15 | SES | 2014-15 | 0 | 46.034 | 0
SES16 | SES | 2015-16 | 0 | 44.7511 | 0
SES17 | SES | 2016-17 | 0 | 49.3363 | 0
SES18 | SES | 2017-18 | 0 | 51.205 | 0
SES19 | SES | 2018-19 | 0 | 52.3625 | 0
SES20 | SES | 2019-20 | 0 | 53.7106 | 0
SES21 | SES | 2020-21 | 0 | 52.777 | 0
SES22 | SES | 2021-22 | 0 | 57.544 | 0
SES23 | SES | 2022-23 | 0 | 52.131 | 0
SES24 | SES | 2023-24 | 0 | 46.371 | 0
SES25 | SES | 2024-25 | 0 | 45.346 | 0
SEW12 | SEW | 2011-12 | 0 | 158.0452 | 0
SEW13 | SEW | 2012-13 | 0 | 166.4331 | 0
SEW14 | SEW | 2013-14 | 0 | 171.0139 | 0
SEW15 | SEW | 2014-15 | 0 | 167.4904 | 0
SEW16 | SEW | 2015-16 | 0.11549 | 161.5074 | 0
SEW17 | SEW | 2016-17 | 0 | 162.5752 | 0
SEW18 | SEW | 2017-18 | 0 | 171.97 | 0
SEW19 | SEW | 2018-19 | 0 | 180.8624 | 0
SEW20 | SEW | 2019-20 | 0 | 169.0072 | 0
SEW21 | SEW | 2020-21 | 0 | 172.073 | 0
SEW22 | SEW | 2021-22 | 0 | 199.614 | 0
SEW23 | SEW | 2022-23 | 0 | 208.204 | 0
SEW24 | SEW | 2023-24 | 0 | 186.195 | 0
SEW25 | SEW | 2024-25 | 0 | 194.588 | 0
SSC12 | SSC | 2011-12 | 0 | 79.0064 | 0
SSC13 | SSC | 2012-13 | 0 | 86.0693 | 0
SSC14 | SSC | 2013-14 | 0 | 80.0066 | 0
SSC15 | SSC | 2014-15 | 0 | 80.0541 | 0
SSC16 | SSC | 2015-16 | 0 | 83.4035 | 0
SSC17 | SSC | 2016-17 | 0 | 87.873 | 0
SSC18 | SSC | 2017-18 | 0 | 95.2708 | 0
SSC19 | SSC | 2018-19 | 0 | 91.7522 | 0
SSC20 | SSC | 2019-20 | 0 | 91.6349 | 0
SSC21 | SSC | 2020-21 | 22.7288 | 113.2581 | 0
SSC22 | SSC | 2021-22 | 22.7288 | 115.4825 | 0
SSC23 | SSC | 2022-23 | 23.7464 | 116.3865 | 1.0793
SSC24 | SSC | 2023-24 | 1.0177 | 93.9133 | 1.0327
SSC25 | SSC | 2024-25 | 1.0177 | 96.8046 | 0.99775
SVE12 | SVE | 2011-12 | 0 | 0 | 0
SVE13 | SVE | 2012-13 | 0 | 0 | 0
SVE14 | SVE | 2013-14 | 0 | 0 | 0
SVE15 | SVE | 2014-15 | 0 | 0 | 0
SVE16 | SVE | 2015-16 | 0 | 0 | 0
SVE17 | SVE | 2016-17 | 0 | 0 | 0
SVE18 | SVE | 2017-18 | 3.812 | 687.9725 | 2.1604
SVE19 | SVE | 2018-19 | 0.050059 | 757.2387 | 2.2339
SVE20 | SVE | 2019-20 | -0.11395 | 799.0685 | 2.3022
SVE21 | SVE | 2020-21 | 0 | 575.0657 | 4.1456
SVE22 | SVE | 2021-22 | 0 | 631.1286 | 4.1502
SVE23 | SVE | 2022-23 | 0 | 643.4347 | 4.2291
SVE24 | SVE | 2023-24 | 0 | 635.4116 | 4.704
SVE25 | SVE | 2024-25 | 0 | 630.7635 | 5.2157
HDD12 | HDD | 2011-12 | 0 | 0 | 0
HDD13 | HDD | 2012-13 | 0 | 0 | 0
HDD14 | HDD | 2013-14 | 0 | 0 | 0
HDD15 | HDD | 2014-15 | 0 | 0 | 0
HDD16 | HDD | 2015-16 | 0 | 0 | 0
HDD17 | HDD | 2016-17 | 0 | 0 | 0
HDD18 | HDD | 2017-18 | 0 | 28.8835 | 0
HDD19 | HDD | 2018-19 | 0 | 31.6394 | 0
HDD20 | HDD | 2019-20 | 0 | 24.7939 | 0
HDD21 | HDD | 2020-21 | 0 | 27.46 | 0.036411
HDD22 | HDD | 2021-22 | 0 | 27.121 | 0.056411
HDD23 | HDD | 2022-23 | 0.53196 | 26.327 | 0.041411
HDD24 | HDD | 2023-24 | 0.53196 | 25.742 | 0.041411
HDD25 | HDD | 2024-25 | 0.53196 | 26.044 | 0.041411
|  |  | 342.4984 | 66767.8566 | 34.7866

## Data_Override
Data
£m 2017-18 prices
|  |  | C_W3003CAW_PR19CA001 | C_W3026TECAW_PR19CA001 | WS2013CAW
Code | Company | Year | £m, Enhancement capex water - Improving taste / odour / colour | £m 2017-18 prices, Totex wholesale water (including cash items and atypical expenditure) | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total | Comments on override
ANH12 | ANH | 2011-12
ANH13 | ANH | 2012-13
ANH14 | ANH | 2013-14
ANH15 | ANH | 2014-15
ANH16 | ANH | 2015-16
ANH17 | ANH | 2016-17
ANH18 | ANH | 2017-18
ANH19 | ANH | 2018-19
ANH20 | ANH | 2019-20
ANH21 | ANH | 2020-21
ANH22 | ANH | 2021-22
ANH23 | ANH | 2022-23
ANH24 | ANH | 2023-24
ANH25 | ANH | 2024-25
NES12 | NES | 2011-12
NES13 | NES | 2012-13
NES14 | NES | 2013-14
NES15 | NES | 2014-15
NES16 | NES | 2015-16
NES17 | NES | 2016-17
NES18 | NES | 2017-18
NES19 | NES | 2018-19
NES20 | NES | 2019-20
NES21 | NES | 2020-21
NES22 | NES | 2021-22
NES23 | NES | 2022-23
NES24 | NES | 2023-24
NES25 | NES | 2024-25
NWT12 | NWT | 2011-12
NWT13 | NWT | 2012-13
NWT14 | NWT | 2013-14
NWT15 | NWT | 2014-15
NWT16 | NWT | 2015-16
NWT17 | NWT | 2016-17
NWT18 | NWT | 2017-18
NWT19 | NWT | 2018-19
NWT20 | NWT | 2019-20
NWT21 | NWT | 2020-21
NWT22 | NWT | 2021-22
NWT23 | NWT | 2022-23
NWT24 | NWT | 2023-24
NWT25 | NWT | 2024-25
SRN12 | SRN | 2011-12
SRN13 | SRN | 2012-13
SRN14 | SRN | 2013-14
SRN15 | SRN | 2014-15
SRN16 | SRN | 2015-16
SRN17 | SRN | 2016-17
SRN18 | SRN | 2017-18
SRN19 | SRN | 2018-19
SRN20 | SRN | 2019-20
SRN21 | SRN | 2020-21
SRN22 | SRN | 2021-22
SRN23 | SRN | 2022-23
SRN24 | SRN | 2023-24
SRN25 | SRN | 2024-25
SVT12 | SVT | 2011-12
SVT13 | SVT | 2012-13
SVT14 | SVT | 2013-14
SVT15 | SVT | 2014-15
SVT16 | SVT | 2015-16
SVT17 | SVT | 2016-17
SVT18 | SVT | 2017-18
SVT19 | SVT | 2018-19
SVT20 | SVT | 2019-20
SVT21 | SVT | 2020-21
SVT22 | SVT | 2021-22
SVT23 | SVT | 2022-23
SVT24 | SVT | 2023-24
SVT25 | SVT | 2024-25
SWT12 | SWT | 2011-12
SWT13 | SWT | 2012-13
SWT14 | SWT | 2013-14
SWT15 | SWT | 2014-15
SWT16 | SWT | 2015-16
SWT17 | SWT | 2016-17
SWT18 | SWT | 2017-18
SWT19 | SWT | 2018-19
SWT20 | SWT | 2019-20
SWT21 | SWT | 2020-21
SWT22 | SWT | 2021-22
SWT23 | SWT | 2022-23
SWT24 | SWT | 2023-24
SWT25 | SWT | 2024-25
SWB17 | SWB | 2016-17
SWB18 | SWB | 2017-18
SWB19 | SWB | 2018-19
SWB20 | SWB | 2019-20
SWB21 | SWB | 2020-21
SWB22 | SWB | 2021-22
SWB23 | SWB | 2022-23
SWB24 | SWB | 2023-24
SWB25 | SWB | 2024-25
TMS12 | TMS | 2011-12
TMS13 | TMS | 2012-13
TMS14 | TMS | 2013-14
TMS15 | TMS | 2014-15
TMS16 | TMS | 2015-16
TMS17 | TMS | 2016-17
TMS18 | TMS | 2017-18
TMS19 | TMS | 2018-19
TMS20 | TMS | 2019-20
TMS21 | TMS | 2020-21
TMS22 | TMS | 2021-22
TMS23 | TMS | 2022-23
TMS24 | TMS | 2023-24
TMS25 | TMS | 2024-25
WSH12 | WSH | 2011-12
WSH13 | WSH | 2012-13
WSH14 | WSH | 2013-14
WSH15 | WSH | 2014-15
WSH16 | WSH | 2015-16
WSH17 | WSH | 2016-17
WSH18 | WSH | 2017-18
WSH19 | WSH | 2018-19
WSH20 | WSH | 2019-20
WSH21 | WSH | 2020-21
WSH22 | WSH | 2021-22
WSH23 | WSH | 2022-23
WSH24 | WSH | 2023-24
WSH25 | WSH | 2024-25
WSX12 | WSX | 2011-12
WSX13 | WSX | 2012-13
WSX14 | WSX | 2013-14
WSX15 | WSX | 2014-15
WSX16 | WSX | 2015-16
WSX17 | WSX | 2016-17
WSX18 | WSX | 2017-18
WSX19 | WSX | 2018-19
WSX20 | WSX | 2019-20
WSX21 | WSX | 2020-21
WSX22 | WSX | 2021-22
WSX23 | WSX | 2022-23
WSX24 | WSX | 2023-24
WSX25 | WSX | 2024-25
YKY12 | YKY | 2011-12
YKY13 | YKY | 2012-13
YKY14 | YKY | 2013-14
YKY15 | YKY | 2014-15
YKY16 | YKY | 2015-16
YKY17 | YKY | 2016-17
YKY18 | YKY | 2017-18
YKY19 | YKY | 2018-19
YKY20 | YKY | 2019-20
YKY21 | YKY | 2020-21
YKY22 | YKY | 2021-22
YKY23 | YKY | 2022-23
YKY24 | YKY | 2023-24
YKY25 | YKY | 2024-25
AFW12 | AFW | 2011-12
AFW13 | AFW | 2012-13
AFW14 | AFW | 2013-14
AFW15 | AFW | 2014-15
AFW16 | AFW | 2015-16
AFW17 | AFW | 2016-17
AFW18 | AFW | 2017-18
AFW19 | AFW | 2018-19
AFW20 | AFW | 2019-20
AFW21 | AFW | 2020-21
AFW22 | AFW | 2021-22
AFW23 | AFW | 2022-23
AFW24 | AFW | 2023-24
AFW25 | AFW | 2024-25
BRL12 | BRL | 2011-12
BRL13 | BRL | 2012-13
BRL14 | BRL | 2013-14
BRL15 | BRL | 2014-15
BRL16 | BRL | 2015-16
BRL17 | BRL | 2016-17
BRL18 | BRL | 2017-18
BRL19 | BRL | 2018-19
BRL20 | BRL | 2019-20
BRL21 | BRL | 2020-21
BRL22 | BRL | 2021-22
BRL23 | BRL | 2022-23
BRL24 | BRL | 2023-24
BRL25 | BRL | 2024-25
BWH12 | BWH | 2011-12
BWH13 | BWH | 2012-13
BWH14 | BWH | 2013-14
BWH15 | BWH | 2014-15
BWH16 | BWH | 2015-16
BWH17 | BWH | 2016-17
BWH18 | BWH | 2017-18
BWH19 | BWH | 2018-19
BWH20 | BWH | 2019-20
BWH21 | BWH | 2020-21
BWH22 | BWH | 2021-22
BWH23 | BWH | 2022-23
BWH24 | BWH | 2023-24
BWH25 | BWH | 2024-25
DVW12 | DVW | 2011-12
DVW13 | DVW | 2012-13
DVW14 | DVW | 2013-14
DVW15 | DVW | 2014-15
DVW16 | DVW | 2015-16
DVW17 | DVW | 2016-17
DVW18 | DVW | 2017-18
DVW19 | DVW | 2018-19
DVW20 | DVW | 2019-20
DVW21 | DVW | 2020-21
DVW22 | DVW | 2021-22
DVW23 | DVW | 2022-23
DVW24 | DVW | 2023-24
DVW25 | DVW | 2024-25
PRT12 | PRT | 2011-12
PRT13 | PRT | 2012-13
PRT14 | PRT | 2013-14
PRT15 | PRT | 2014-15
PRT16 | PRT | 2015-16
PRT17 | PRT | 2016-17
PRT18 | PRT | 2017-18
PRT19 | PRT | 2018-19
PRT20 | PRT | 2019-20
PRT21 | PRT | 2020-21
PRT22 | PRT | 2021-22
PRT23 | PRT | 2022-23
PRT24 | PRT | 2023-24
PRT25 | PRT | 2024-25
SES12 | SES | 2011-12
SES13 | SES | 2012-13
SES14 | SES | 2013-14
SES15 | SES | 2014-15
SES16 | SES | 2015-16
SES17 | SES | 2016-17
SES18 | SES | 2017-18
SES19 | SES | 2018-19
SES20 | SES | 2019-20
SES21 | SES | 2020-21
SES22 | SES | 2021-22
SES23 | SES | 2022-23
SES24 | SES | 2023-24
SES25 | SES | 2024-25
SEW12 | SEW | 2011-12
SEW13 | SEW | 2012-13
SEW14 | SEW | 2013-14
SEW15 | SEW | 2014-15
SEW16 | SEW | 2015-16
SEW17 | SEW | 2016-17
SEW18 | SEW | 2017-18
SEW19 | SEW | 2018-19
SEW20 | SEW | 2019-20
SEW21 | SEW | 2020-21
SEW22 | SEW | 2021-22
SEW23 | SEW | 2022-23
SEW24 | SEW | 2023-24
SEW25 | SEW | 2024-25
SSC12 | SSC | 2011-12
SSC13 | SSC | 2012-13
SSC14 | SSC | 2013-14
SSC15 | SSC | 2014-15
SSC16 | SSC | 2015-16
SSC17 | SSC | 2016-17
SSC18 | SSC | 2017-18
SSC19 | SSC | 2018-19
SSC20 | SSC | 2019-20
SSC21 | SSC | 2020-21
SSC22 | SSC | 2021-22
SSC23 | SSC | 2022-23
SSC24 | SSC | 2023-24
SSC25 | SSC | 2024-25
SVE12 | SVE | 2011-12
SVE13 | SVE | 2012-13
SVE14 | SVE | 2013-14
SVE15 | SVE | 2014-15
SVE16 | SVE | 2015-16
SVE17 | SVE | 2016-17
SVE18 | SVE | 2017-18
SVE19 | SVE | 2018-19
SVE20 | SVE | 2019-20
SVE21 | SVE | 2020-21 |  |  | 1.922 | AF: Taken 2.223 from value to rebase to 1 April 2020. (2.223 is 2.302 in 2017-18 prices)
SVE22 | SVE | 2021-22 |  |  | 1.927 | AF: Taken 2.223 from value to rebase to 1 April 2020. (2.223 is 2.302 in 2017-18 prices)
SVE23 | SVE | 2022-23 |  |  | 2.006 | AF: Taken 2.223 from value to rebase to 1 April 2020. (2.223 is 2.302 in 2017-18 prices)
SVE24 | SVE | 2023-24 |  |  | 2.481 | AF: Taken 2.223 from value to rebase to 1 April 2020. (2.223 is 2.302 in 2017-18 prices)
SVE25 | SVE | 2024-25 |  |  | 2.992 | AF: Taken 2.223 from value to rebase to 1 April 2020. (2.223 is 2.302 in 2017-18 prices)
HDD12 | HDD | 2011-12
HDD13 | HDD | 2012-13
HDD14 | HDD | 2013-14
HDD15 | HDD | 2014-15
HDD16 | HDD | 2015-16
HDD17 | HDD | 2016-17
HDD18 | HDD | 2017-18
HDD19 | HDD | 2018-19
HDD20 | HDD | 2019-20
HDD21 | HDD | 2020-21
HDD22 | HDD | 2021-22
HDD23 | HDD | 2022-23
HDD24 | HDD | 2023-24
HDD25 | HDD | 2024-25

## Data_Final
Data
£m 2017-18 prices
|  |  | C_W3003CAW_PR19CA001 | C_W3026TECAW_PR19CA001 | WS2013CAW
Code | Company | Year | £m, Enhancement capex water - Improving taste / odour / colour | £m 2017-18 prices, Totex wholesale water (including cash items and atypical expenditure) | Enhancement expenditure by purpose ~ operating - Improving taste / odour / colour - Total
ANH12 | ANH | 2011-12 | 0 | 369.5998 | 0
ANH13 | ANH | 2012-13 | 0 | 393.9067 | 0
ANH14 | ANH | 2013-14 | 0 | 354.537 | 0
ANH15 | ANH | 2014-15 | 0.23471 | 370.2469 | 0
ANH16 | ANH | 2015-16 | 0.015557 | 327.6219 | 0
ANH17 | ANH | 2016-17 | 0.0016389 | 375.7071 | 0
ANH18 | ANH | 2017-18 | -0.0046807 | 399.9078 | 0
ANH19 | ANH | 2018-19 | 0.0048399 | 442.6981 | 0
ANH20 | ANH | 2019-20 | 0 | 397.8529 | 0
ANH21 | ANH | 2020-21 | 0 | 494.8537 | 0
ANH22 | ANH | 2021-22 | 0 | 569.1626 | 0
ANH23 | ANH | 2022-23 | 0 | 614.4832 | 0
ANH24 | ANH | 2023-24 | 0 | 601.174 | 0
ANH25 | ANH | 2024-25 | 0 | 466.5721 | 0
NES12 | NES | 2011-12 | 2.1162 | 334.7369 | 0
NES13 | NES | 2012-13 | -0.035608 | 301.2122 | 0
NES14 | NES | 2013-14 | -0.0042279 | 287.3082 | 0
NES15 | NES | 2014-15 | 0 | 277.2513 | 0
NES16 | NES | 2015-16 | 0.07179 | 291.5084 | 0
NES17 | NES | 2016-17 | 3.7492 | 284.6257 | 0
NES18 | NES | 2017-18 | 5.544 | 344.341 | 0.078
NES19 | NES | 2018-19 | 2.5245 | 367.7514 | 0
NES20 | NES | 2019-20 | 0.31414 | 334.5254 | 0.061
NES21 | NES | 2020-21 | 0 | 348.078 | 0
NES22 | NES | 2021-22 | 0 | 368.717 | 0
NES23 | NES | 2022-23 | 0 | 360.499 | 0
NES24 | NES | 2023-24 | 0 | 337.229 | 0
NES25 | NES | 2024-25 | 0 | 311.733 | 0
NWT12 | NWT | 2011-12 | 33.1847 | 531.2972 | 0
NWT13 | NWT | 2012-13 | 34.8986 | 554.3658 | 0
NWT14 | NWT | 2013-14 | 21.5808 | 550.9866 | 0
NWT15 | NWT | 2014-15 | 13.4925 | 545.1088 | 0
NWT16 | NWT | 2015-16 | 0.85435 | 549.5249 | 0
NWT17 | NWT | 2016-17 | 0.51343 | 612.8371 | 0
NWT18 | NWT | 2017-18 | 1.1735 | 601.4976 | 0
NWT19 | NWT | 2018-19 | 4.2692 | 621.8529 | 0
NWT20 | NWT | 2019-20 | 0.057749 | 528.1722 | 0
NWT21 | NWT | 2020-21 | 1.3802 | 546.9142 | 0.3633
NWT22 | NWT | 2021-22 | 1.8995 | 511.026 | 0.3657
NWT23 | NWT | 2022-23 | 4.0644 | 491.8832 | 0.36753
NWT24 | NWT | 2023-24 | 1.3693 | 466.2618 | 0.3688
NWT25 | NWT | 2024-25 | 1.3033 | 461.4183 | 0.37008
SRN12 | SRN | 2011-12 | -0.0022101 | 208.0852 | 0
SRN13 | SRN | 2012-13 | 0.025897 | 162.4407 | 0
SRN14 | SRN | 2013-14 | 0 | 158.0999 | 0
SRN15 | SRN | 2014-15 | 0 | 150.6366 | 0
SRN16 | SRN | 2015-16 | 0 | 132.0083 | 0
SRN17 | SRN | 2016-17 | 0 | 165.5298 | 0
SRN18 | SRN | 2017-18 | 0 | 227.072 | 0
SRN19 | SRN | 2018-19 | 0 | 212.6489 | 0
SRN20 | SRN | 2019-20 | 0 | 211.2972 | 0
SRN21 | SRN | 2020-21 | 0 | 238.969 | 0
SRN22 | SRN | 2021-22 | 0 | 240.008 | 0
SRN23 | SRN | 2022-23 | 0 | 219.66 | 0
SRN24 | SRN | 2023-24 | 0 | 201.802 | 0
SRN25 | SRN | 2024-25 | 0 | 217.626 | 0
SVT12 | SVT | 2011-12 | 0.13022 | 518.0027 | 0
SVT13 | SVT | 2012-13 | -0.012948 | 557.0869 | 0
SVT14 | SVT | 2013-14 | 0.54818 | 583.1486 | 0
SVT15 | SVT | 2014-15 | 3.4035 | 611.9245 | 0
SVT16 | SVT | 2015-16 | 7.2752 | 587.1872 | 0
SVT17 | SVT | 2016-17 | 1.2399 | 609.9451 | 0
SVT18 | SVT | 2017-18 | 1.111 | 683.786 | 0
SVT19 | SVT | 2018-19 | 0 | 0 | 0
SVT20 | SVT | 2019-20 | 0 | 0 | 0
SVT21 | SVT | 2020-21 | 0 | 0 | 0
SVT22 | SVT | 2021-22 | 0 | 0 | 0
SVT23 | SVT | 2022-23 | 0 | 0 | 0
SVT24 | SVT | 2023-24 | 0 | 0 | 0
SVT25 | SVT | 2024-25 | 0 | 0 | 0
SWT12 | SWT | 2011-12 | 0 | 140.7011 | 0
SWT13 | SWT | 2012-13 | 0 | 113.3753 | 0
SWT14 | SWT | 2013-14 | 0 | 129.4919 | 0
SWT15 | SWT | 2014-15 | 0 | 130.1755 | 0
SWT16 | SWT | 2015-16 | 0 | 128.9304 | 0
SWT17 | SWT | 2016-17 | 0 | 0 | 0
SWT18 | SWT | 2017-18 | 0 | 0 | 0
SWT19 | SWT | 2018-19 | 0 | 0 | 0
SWT20 | SWT | 2019-20 | 0 | 0 | 0
SWT21 | SWT | 2020-21 | 0 | 0 | 0
SWT22 | SWT | 2021-22 | 0 | 0 | 0
SWT23 | SWT | 2022-23 | 0 | 0 | 0
SWT24 | SWT | 2023-24 | 0 | 0 | 0
SWT25 | SWT | 2024-25 | 0 | 0 | 0
SWB17 | SWB | 2016-17 | 0 | 171.9259 | 0
SWB18 | SWB | 2017-18 | 0 | 175.102 | 0
SWB19 | SWB | 2018-19 | 0 | 146.7962 | 0
SWB20 | SWB | 2019-20 | 0 | 138.7275 | 0
SWB21 | SWB | 2020-21 | 1.56 | 164.926 | 0
SWB22 | SWB | 2021-22 | 1.56 | 179.669 | 0
SWB23 | SWB | 2022-23 | 1.56 | 192.194 | 0
SWB24 | SWB | 2023-24 | 1.56 | 181.702 | 0
SWB25 | SWB | 2024-25 | 1.56 | 175.761 | 0
TMS12 | TMS | 2011-12 | 0 | 655.6572 | 0
TMS13 | TMS | 2012-13 | 0 | 618.3888 | 0
TMS14 | TMS | 2013-14 | 0 | 634.9723 | 0
TMS15 | TMS | 2014-15 | 0 | 682.7605 | 0
TMS16 | TMS | 2015-16 | 0 | 747.529 | 0
TMS17 | TMS | 2016-17 | 0 | 849.161 | 0
TMS18 | TMS | 2017-18 | 0 | 895.282 | 0
TMS19 | TMS | 2018-19 | 0 | 960.4243 | 0
TMS20 | TMS | 2019-20 | 0 | 1024.5945 | 0
TMS21 | TMS | 2020-21 | 0 | 1009.8378 | 0
TMS22 | TMS | 2021-22 | 0 | 1101.9036 | 0
TMS23 | TMS | 2022-23 | 0 | 1077.4233 | 0
TMS24 | TMS | 2023-24 | 0 | 1033.9695 | 0
TMS25 | TMS | 2024-25 | 0 | 997.9188 | 0
WSH12 | WSH | 2011-12 | 2.9008 | 273.9076 | 0
WSH13 | WSH | 2012-13 | 0.88265 | 296.8508 | 0
WSH14 | WSH | 2013-14 | 1.67 | 299.6694 | 0
WSH15 | WSH | 2014-15 | 3.8959 | 330.2704 | 0
WSH16 | WSH | 2015-16 | 4.3386 | 238.9135 | 0
WSH17 | WSH | 2016-17 | 1.3096 | 320.2603 | 0
WSH18 | WSH | 2017-18 | 7.664 | 354.3857 | 0.05
WSH19 | WSH | 2018-19 | 10.8012 | 342.0294 | 0.05
WSH20 | WSH | 2019-20 | 7.4638 | 300.7342 | 0.05
WSH21 | WSH | 2020-21 | 8.066 | 338.873 | 0.008
WSH22 | WSH | 2021-22 | 7.656 | 347.164 | 0.008
WSH23 | WSH | 2022-23 | 6.171 | 338.818 | 0.008
WSH24 | WSH | 2023-24 | 2.653 | 324.732 | 0.008
WSH25 | WSH | 2024-25 | 2.633 | 316.383 | 0.008
WSX12 | WSX | 2011-12 | 2.2256 | 160.1115 | 0
WSX13 | WSX | 2012-13 | 6.2357 | 176.2073 | 0
WSX14 | WSX | 2013-14 | 2.8189 | 161.725 | 0
WSX15 | WSX | 2014-15 | 0.76706 | 155.7696 | 0
WSX16 | WSX | 2015-16 | 0.13096 | 161.7977 | 0
WSX17 | WSX | 2016-17 | 1.0007 | 157.5438 | 0
WSX18 | WSX | 2017-18 | 1.7063 | 135.1825 | 0
WSX19 | WSX | 2018-19 | 0 | 135.5478 | -0.038669
WSX20 | WSX | 2019-20 | 0 | 145.6387 | 0
WSX21 | WSX | 2020-21 | 0 | 134.2655 | 0
WSX22 | WSX | 2021-22 | 0 | 125.5988 | 0
WSX23 | WSX | 2022-23 | 0 | 144.2895 | 0
WSX24 | WSX | 2023-24 | 0 | 125.3448 | 0
WSX25 | WSX | 2024-25 | 0 | 120.5543 | 0
YKY12 | YKY | 2011-12 | 0 | 390.8034 | 0
YKY13 | YKY | 2012-13 | 0 | 309.4734 | 0
YKY14 | YKY | 2013-14 | 0 | 263.5993 | 0
YKY15 | YKY | 2014-15 | 0 | 271.3183 | 0
YKY16 | YKY | 2015-16 | 0 | 295.5084 | 0
YKY17 | YKY | 2016-17 | 0 | 337.3085 | 0
YKY18 | YKY | 2017-18 | 0 | 369.595 | 0
YKY19 | YKY | 2018-19 | 0 | 414.498 | 0
YKY20 | YKY | 2019-20 | 0 | 394.0111 | 0
YKY21 | YKY | 2020-21 | 4.75 | 385.797 | 0
YKY22 | YKY | 2021-22 | 4.437 | 385.065 | 0
YKY23 | YKY | 2022-23 | 3.45 | 393.66 | 0
YKY24 | YKY | 2023-24 | 2.276 | 376.679 | 0
YKY25 | YKY | 2024-25 | 1.901 | 345.664 | 0.193
AFW12 | AFW | 2011-12 | 0 | 212.9247 | 0
AFW13 | AFW | 2012-13 | 0 | 219.3039 | 0
AFW14 | AFW | 2013-14 | 0 | 224.1049 | 0
AFW15 | AFW | 2014-15 | 0 | 216.4519 | 0
AFW16 | AFW | 2015-16 | 1.7927 | 237.3466 | 0
AFW17 | AFW | 2016-17 | 3.2648 | 275.8073 | 0
AFW18 | AFW | 2017-18 | 0.613 | 255.5782 | 0
AFW19 | AFW | 2018-19 | 0 | 240.0907 | 0
AFW20 | AFW | 2019-20 | 0 | 226.3173 | 0
AFW21 | AFW | 2020-21 | 0 | 287.61 | 0
AFW22 | AFW | 2021-22 | 0 | 290.6915 | 0
AFW23 | AFW | 2022-23 | 0 | 281.3912 | 0
AFW24 | AFW | 2023-24 | 0 | 264.4597 | 0
AFW25 | AFW | 2024-25 | 0 | 241.8721 | 0
BRL12 | BRL | 2011-12 | 0 | 106.8552 | 0
BRL13 | BRL | 2012-13 | 0 | 136.6866 | 0
BRL14 | BRL | 2013-14 | 0 | 124.5262 | 0
BRL15 | BRL | 2014-15 | 0 | 111.4734 | 0
BRL16 | BRL | 2015-16 | 0 | 74.0819 | 0
BRL17 | BRL | 2016-17 | 0 | 85.1219 | 0
BRL18 | BRL | 2017-18 | 0 | 103.363 | 0
BRL19 | BRL | 2018-19 | 0 | 104.8207 | 0
BRL20 | BRL | 2019-20 | 0 | 101.8476 | 0
BRL21 | BRL | 2020-21 | 0 | 91.388 | 0
BRL22 | BRL | 2021-22 | 0 | 89.27 | 0
BRL23 | BRL | 2022-23 | 0 | 89.474 | 0
BRL24 | BRL | 2023-24 | 0 | 89.114 | 0
BRL25 | BRL | 2024-25 | 0 | 89.552 | 0
BWH12 | BWH | 2011-12 | 0 | 27.8454 | 0
BWH13 | BWH | 2012-13 | 0 | 26.1622 | 0
BWH14 | BWH | 2013-14 | 0 | 30.2651 | 0
BWH15 | BWH | 2014-15 | 0 | 28.3885 | 0
BWH16 | BWH | 2015-16 | 0 | 26.0358 | 0
BWH17 | BWH | 2016-17 | 0 | 0 | 0
BWH18 | BWH | 2017-18 | 0 | 0 | 0
BWH19 | BWH | 2018-19 | 0 | 0 | 0
BWH20 | BWH | 2019-20 | 0 | 0 | 0
BWH21 | BWH | 2020-21 | 0 | 0 | 0
BWH22 | BWH | 2021-22 | 0 | 0 | 0
BWH23 | BWH | 2022-23 | 0 | 0 | 0
BWH24 | BWH | 2023-24 | 0 | 0 | 0
BWH25 | BWH | 2024-25 | 0 | 0 | 0
DVW12 | DVW | 2011-12 | 0 | 18.4007 | 0
DVW13 | DVW | 2012-13 | 0 | 24.2402 | 0
DVW14 | DVW | 2013-14 | 0 | 15.9632 | 0
DVW15 | DVW | 2014-15 | 0 | 17.1151 | 0
DVW16 | DVW | 2015-16 | 0.13557 | 16.9084 | 0
DVW17 | DVW | 2016-17 | 1.3626 | 22.0046 | 0
DVW18 | DVW | 2017-18 | 2.713 | 27.924 | 0
DVW19 | DVW | 2018-19 | 0 | 0 | 0
DVW20 | DVW | 2019-20 | 0 | 0 | 0
DVW21 | DVW | 2020-21 | 0 | 0 | 0
DVW22 | DVW | 2021-22 | 0 | 0 | 0
DVW23 | DVW | 2022-23 | 0 | 0 | 0
DVW24 | DVW | 2023-24 | 0 | 0 | 0
DVW25 | DVW | 2024-25 | 0 | 0 | 0
PRT12 | PRT | 2011-12 | 0.011051 | 28.1062 | 0
PRT13 | PRT | 2012-13 | 0.0053952 | 32.8684 | 0
PRT14 | PRT | 2013-14 | 0.0042279 | 27.5265 | 0
PRT15 | PRT | 2014-15 | 0 | 27.2787 | 0
PRT16 | PRT | 2015-16 | 0 | 28.6556 | 0
PRT17 | PRT | 2016-17 | 0 | 32.4848 | 0
PRT18 | PRT | 2017-18 | 0 | 27.996 | 0
PRT19 | PRT | 2018-19 | 0 | 36.0049 | 0
PRT20 | PRT | 2019-20 | 0 | 35.8795 | 0
PRT21 | PRT | 2020-21 | 0 | 45.14 | 0
PRT22 | PRT | 2021-22 | 0 | 38.365 | 0
PRT23 | PRT | 2022-23 | 0 | 39.048 | 0
PRT24 | PRT | 2023-24 | 0 | 51.654 | 0
PRT25 | PRT | 2024-25 | 0 | 53.923 | 0
SES12 | SES | 2011-12 | 0 | 52.1689 | 0
SES13 | SES | 2012-13 | 0 | 46.4448 | 0
SES14 | SES | 2013-14 | 0 | 48.576 | 0
SES15 | SES | 2014-15 | 0 | 46.034 | 0
SES16 | SES | 2015-16 | 0 | 44.7511 | 0
SES17 | SES | 2016-17 | 0 | 49.3363 | 0
SES18 | SES | 2017-18 | 0 | 51.205 | 0
SES19 | SES | 2018-19 | 0 | 52.3625 | 0
SES20 | SES | 2019-20 | 0 | 53.7106 | 0
SES21 | SES | 2020-21 | 0 | 52.777 | 0
SES22 | SES | 2021-22 | 0 | 57.544 | 0
SES23 | SES | 2022-23 | 0 | 52.131 | 0
SES24 | SES | 2023-24 | 0 | 46.371 | 0
SES25 | SES | 2024-25 | 0 | 45.346 | 0
SEW12 | SEW | 2011-12 | 0 | 158.0452 | 0
SEW13 | SEW | 2012-13 | 0 | 166.4331 | 0
SEW14 | SEW | 2013-14 | 0 | 171.0139 | 0
SEW15 | SEW | 2014-15 | 0 | 167.4904 | 0
SEW16 | SEW | 2015-16 | 0.11549 | 161.5074 | 0
SEW17 | SEW | 2016-17 | 0 | 162.5752 | 0
SEW18 | SEW | 2017-18 | 0 | 171.97 | 0
SEW19 | SEW | 2018-19 | 0 | 180.8624 | 0
SEW20 | SEW | 2019-20 | 0 | 169.0072 | 0
SEW21 | SEW | 2020-21 | 0 | 172.073 | 0
SEW22 | SEW | 2021-22 | 0 | 199.614 | 0
SEW23 | SEW | 2022-23 | 0 | 208.204 | 0
SEW24 | SEW | 2023-24 | 0 | 186.195 | 0
SEW25 | SEW | 2024-25 | 0 | 194.588 | 0
SSC12 | SSC | 2011-12 | 0 | 79.0064 | 0
SSC13 | SSC | 2012-13 | 0 | 86.0693 | 0
SSC14 | SSC | 2013-14 | 0 | 80.0066 | 0
SSC15 | SSC | 2014-15 | 0 | 80.0541 | 0
SSC16 | SSC | 2015-16 | 0 | 83.4035 | 0
SSC17 | SSC | 2016-17 | 0 | 87.873 | 0
SSC18 | SSC | 2017-18 | 0 | 95.2708 | 0
SSC19 | SSC | 2018-19 | 0 | 91.7522 | 0
SSC20 | SSC | 2019-20 | 0 | 91.6349 | 0
SSC21 | SSC | 2020-21 | 22.7288 | 113.2581 | 0
SSC22 | SSC | 2021-22 | 22.7288 | 115.4825 | 0
SSC23 | SSC | 2022-23 | 23.7464 | 116.3865 | 1.0793
SSC24 | SSC | 2023-24 | 1.0177 | 93.9133 | 1.0327
SSC25 | SSC | 2024-25 | 1.0177 | 96.8046 | 0.99775
SVE12 | SVE | 2011-12 | 0 | 0 | 0
SVE13 | SVE | 2012-13 | 0 | 0 | 0
SVE14 | SVE | 2013-14 | 0 | 0 | 0
SVE15 | SVE | 2014-15 | 0 | 0 | 0
SVE16 | SVE | 2015-16 | 0 | 0 | 0
SVE17 | SVE | 2016-17 | 0 | 0 | 0
SVE18 | SVE | 2017-18 | 3.812 | 687.9725 | 2.1604
SVE19 | SVE | 2018-19 | 0.050059 | 757.2387 | 2.2339
SVE20 | SVE | 2019-20 | -0.11395 | 799.0685 | 2.3022
SVE21 | SVE | 2020-21 | 0 | 575.0657 | 1.922
SVE22 | SVE | 2021-22 | 0 | 631.1286 | 1.927
SVE23 | SVE | 2022-23 | 0 | 643.4347 | 2.006
SVE24 | SVE | 2023-24 | 0 | 635.4116 | 2.481
SVE25 | SVE | 2024-25 | 0 | 630.7635 | 2.992
HDD12 | HDD | 2011-12 | 0 | 0 | 0
HDD13 | HDD | 2012-13 | 0 | 0 | 0
HDD14 | HDD | 2013-14 | 0 | 0 | 0
HDD15 | HDD | 2014-15 | 0 | 0 | 0
HDD16 | HDD | 2015-16 | 0 | 0 | 0
HDD17 | HDD | 2016-17 | 0 | 0 | 0
HDD18 | HDD | 2017-18 | 0 | 28.8835 | 0
HDD19 | HDD | 2018-19 | 0 | 31.6394 | 0
HDD20 | HDD | 2019-20 | 0 | 24.7939 | 0
HDD21 | HDD | 2020-21 | 0 | 27.46 | 0.036411
HDD22 | HDD | 2021-22 | 0 | 27.121 | 0.056411
HDD23 | HDD | 2022-23 | 0.53196 | 26.327 | 0.041411
HDD24 | HDD | 2023-24 | 0.53196 | 25.742 | 0.041411
HDD25 | HDD | 2024-25 | 0.53196 | 26.044 | 0.041411
|  |  | 342.4984 | 66767.8566 | 23.6701

## Analysis
Analysis and determination of allowance
£m 2017-18 prices
TOTEX
£m, Enhancement totex water - Improving taste / odour / colour
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | AMP7 total | Net reallocations of totex | Totex after reallocations for assessment | Totex carried through to assessment | Comments on overrides | Totex - AMP7 total | Materiality | Assessment methods | Shallow dive efficiency challenge | Shallow dive allowance | Deep dive efficiency challenge
| ANH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 2746.2456 | 0% | Shallow dive | 10% | 0 | 10%
| HDD | 0.036411 | 0.056411 | 0.57337 | 0.57337 | 0.57337 | 1.8129 | 0 | 1.8129 | 1.8129 | n/a | 132.694 | 1.366% | Deep dive | 0% | see deep dive sheet | 5%
| NES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 1726.256 | 0% | Shallow dive | 0.3576% | 0 | 5%
| NWT | 1.7435 | 2.2652 | 4.432 | 1.7381 | 1.6733 | 11.8521 | 0 | 11.8521 | 11.8521 | n/a | 2477.5035 | 0.4784% | Shallow dive | 0% | 11.8521 | 5%
| SRN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 1118.065 | 0% | Shallow dive | 8.33% | 0 | 8.33%
| SVE | 1.922 | 1.927 | 2.006 | 2.481 | 2.992 | 11.328 | 0 | 11.328 | 11.328 | n/a | 3115.8042 | 0.3636% | Shallow dive | 0% | 11.328 | 5%
| SWB | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 7.8 | 0 | 7.8 | 7.8 | n/a | 894.252 | 0.8722% | Deep dive | 0% | see deep dive sheet | 5%
| TMS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 5221.0529 | 0% | Shallow dive | 6.228% | 0 | 6.228%
| WSH | 8.074 | 7.664 | 6.179 | 2.661 | 2.641 | 27.219 | 0 | 27.219 | 27.219 | n/a | 1665.97 | 1.634% | Deep dive | 0% | see deep dive sheet | 5%
| WSX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 650.053 | 0% | Shallow dive | 0% | 0 | 5%
| YKY | 4.75 | 4.437 | 3.45 | 2.276 | 2.094 | 17.007 | 0 | 17.007 | 17.007 | n/a | 1886.865 | 0.9013% | Deep dive | 0% | see deep dive sheet | 5%
| AFW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 1366.0245 | 0% | Shallow dive | 0% | 0 | 5%
| BRL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 448.798 | 0% | Shallow dive | 10% | 0 | 10%
| PRT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 228.13 | 0% | Shallow dive | 0% | 0 | 5%
| SES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 254.169 | 0% | Shallow dive | 0% | 0 | 5%
| SEW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 960.674 | 0% | Shallow dive | 10% | 0 | 10%
| SSC | 22.7288 | 22.7288 | 24.8257 | 2.0504 | 2.0154 | 74.349 | 0 | 74.349 | 0 | Assessed as CAC | 535.8451 | 0% | Deep dive | 4.622% | see deep dive sheet | 5%
| Total | 40.8147 | 40.6384 | 43.0261 | 13.3399 | 13.5491 | 151.3681 | 0 | 151.3681 | 77.0191 |  | 25428.4018 | 0.5953%

## Deep dive_HDD
Deep dive sheet - Hafren Dyfrdwy |  |  |  | Summary at DD
Summary |  |  |  | Summary
Company | HDD |  |  | Company | HDD
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 1.8129 |  |  | Totex carried through deep dive AMP7 (£m) | 1.8129
Totex assessed within cost adjustment claims (£m) |  |  |  | Totex assessed within cost adjustment claims (£m)
Totex assessed within deep dive (£m) | 1.8129 | At final determination the company seeks the same sums as at draft determination. |  | Totex assessed within deep dive (£m) | 1.8129
Totex allowance from cost adjustment claims (£m) |  |  |  | Totex allowance from cost adjustment claims (£m)
Totex allowance from deep dive (£m) | 1.3423 | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this enhancement line. We now correctly apply the company deep dive efficiency challenge. |  | Totex allowance from deep dive (£m) | 1.4129 | As at IAP stage we disallow the cost of the work to air valves and surge protection as we consider these to be base maintenance costs. We allow the remaining cost.
Ofwat view of totex allowance for AMP7 (£m) | 1.3423 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 1.4129
Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | IAP assessment |  |  | References
Need for investment | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Need for investment | Partial pass | As at DD. No change in our assessment. |  | Partial pass | We find no DWI letters of support for this work. However, the need for investment is justified by customer support for the reduction of TOC complaints. HDD identifies a relatively high willingness to pay for resolving TOC complaints [App 5 p28] HDD has set a target reduction in TOC complaints of 38% over 2017-18 levels [BP p146]. Although low in UK terms the target is identified by the company as frontier for companies with similar geology [App2 p10]. |  | App 5 BP P146 App2
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | N/A
Management control | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Management control | Pass | As at DD. No change in our assessment. |  | Pass | Manganese (Mn) in raw waters is outside of management control. Appendix A10 explains the presence of Mn in raw water is due to the underlying geology. |  | Appendix A10
Best option for customers | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Best option for customers | Pass | As at DD. No change in our assessment. | IAP documents: Table Commentary Appendix A4 | Pass | HDD has previously upgraded treatment works and is now seeking to reduce the residual Mn problem with a programme of mains flushing and renewal. [BP p149]. Taste and odour complaints are identified as being of high priority for customers [App 2 p7]. HDD has completed CBA. |  | BP App 2
Robustness and efficiency of costs | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Robustness and efficiency of costs | Partial pass | Capex: In its September BP submission Hafren Dyfrdwy submitted £1.596m and seek the same amount in the April submission. At IAP we disallowed the air valve maintenance and surge protection activities which we costed at £0.400m. We consider these to be base maintenance. in the April submission Hafren Dyfrdwy states "We have reviewed the assessment covering water resources and network plus price controls and overall accept the challenges Ofwat have made, specifically on the enhancement claim on taste/ odour and colour and our Eels obligation under the NEP." [PR19 Revised Business Plan P114]. Therefore our assessment is unchanged from IAP and make the same allowance of £1.196m. Opex: At IAP the company identified a range of opex catchment management schemes [IAP BP P197]. The costs of which are split between the TOC and raw water deterioration opex lines. The company provides a breakdown of these costs [IAP Data Table commentary P26-27]. These are Dee Catchment Partnership £0.153m , Engagement with Farmers £0.029m & Investigation of Algal Blooms £0.035m. The company describes the nature and extent of the work [IAP Appendix A4 P16-18]. In the April BP Hafren Dyfrdwy advises that the metaldehyde ban does not reduce the extent of the work required [HDD Revised BP P 114]. We accept the costs submitted for catchment management schemes and make an allowance of £0.217m. | IAP documents: Table Commentary Appendix A4 DD documents: PR19 HDD Revised Business Plan | Partial pass | "in AMP7 ..... activity such as mains flushing, air valve maintenance and surge protection, which based on current technology and approach is likely to cost between £450,000 and £500,000 in 2017-18 prices across the 2020 to 2025 period. This is based on increasing activity to 20% in both regions (which is the optimum as shown below) at £200 per km for mains flushing (based on cost achieved in AMP6). Also included is maintenance of around 500 air valves that is not in the historic baseline at an estimated range of between £750 and £850 per valve. This represents around 0.5% of totex which will have to be delivered through efficiency savings.[App 2 p10]." HDD proposes "targeting hotspot areas" for the replacement of mains [App2 p8] and also Mn optimisation in its mid-Wales area. No information has been found of the length of mains replacement to be delivered under this enhancement line. HDD has used external consultants KPMG, Arcadis & Turner and Townsend assess cost efficiency [App 5]. HDD has provided evidence of cost efficiencies. However the build-up and scope of the costs lacks clarity. In particular we find insufficient evidence that air valve maintenance and surge protection are enhancement activities. We consider maintenance of these assets as a base cost. Accordingly, we deduct the cost of air valve maintenance [500 air valves at £800 = £400k] in setting our allowance. |  | App2 App5
Customer protection | Partial pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Customer protection | Partial pass | We have not identified any new evidence and retain our assessment from IAP. |  | Partial pass | HDD identifies a WTP for an 'average' TOC complaint. It has uses this when setting a financial ODI for drinking water complaints. The ODI includes outperformance and underperformance. In the absence of DWI letters of support this affords customer protection. |  | App2 P 12
Affordability | N/A |  |  | Affordability | N/A |  |  | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | N/A
[9 empty] | Allowable costs £m [from deep dive] | 1.1959
[9 empty] | Apply Efficiency Challenge | 0%

## Deep dive_SWB
Deep dive sheet - South West Water |  |  |  | Summary at slow track DD
Summary |  |  |  | Summary
Company | SWB |  |  | Company | SWB
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 7.8 | South West Water has not submitted a revised table WS2 for final determination. The Sum sought is as at IAP £7.8m all of which is capex. |  | Totex carried through deep dive AMP7 (£m) | 7.8
Totex assessed within cost adjustment claims (£m) |  |  |  | Totex assessed within cost adjustment claims (£m) |  |  |  | Summary at IAP
Totex assessed within deep dive (£m) | 7.8 |  |  | Totex assessed within deep dive (£m) | 7.8
Totex allowance from cost adjustment claims (£m) |  |  |  | Totex allowance from cost adjustment claims (£m)
Totex allowance from deep dive (£m) | 7.41 |  |  | Totex allowance from deep dive (£m) | 6.327 | Our assessment is unchanged from IAP. As at IAP we apply a company efficiency challenge to set the allowance. |  | Capex carried through deep dive AMP7 (£m) | 7.8
Ofwat view of totex allowance for AMP7 (£m) | 7.41 | The company includes further detail of its programme of mains replacement work in its representation. We now pass the proposed costs and continue to apply the company efficiency challenge to set the allowance. |  | Ofwat view of totex allowance for AMP7 (£m) | 6.327 |  |  | Ofwat view of allowance for AMP7 (£m) | 6.66
Assessment |  |  |  | Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References |  |  |  | References
Need for investment | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Need for investment | Pass | As at IAP. No change in our assessment. |  | Need for investment | Pass | SWB has taste and odour issues at a number of its WTWs and letters of support for investment from the DWI. The company allocates work at WTWs to the raw water deterioration line and a network flushing and rehabilitation to this line. The DWI letter for the network supports the need for the following: * Continuous optimisation of treatment processes with particular regard to manganese removal and particulate matter entering distribution * DMA flushing utilising a risk-based approach to determine flushing priorities. Hydraulic ‘live’ models to be used to aid design of flushing plans. * Where flushing is found to be ineffective in application or outcome, intrusive cleaning or mains rehabilitation is to be considered. * Online monitoring of the Cornwall Spine Main. | DWI Letters of Support Network plus water wholesale revenue control P 19
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | Need for adjustment | N/A
Management control | Partial pass | Sediment is a result of high levels of Manganese [Mn] in the distribution system. South West Water identifies that remobilisation of sediment in the network is the principal cause of taste odour colour (TOC) complaints. The company states that remobilisation of accumulated material in the system is the principal cause of TOC contacts. The company also states that flushing may not be effective the controlled removal of sediments in tuberculated mains. [supporting information P41]. Mn levels entering the water distribution system can be controlled at the treatment works and rehabilitation of tuberculated mains will improve the effectiveness of sewer flushing. As allowance for these has been awarded in previous investment periods we continue to award partial pass. | Securing Cost efficiency - supporting informationvfinal | Management control | Partial pass | Unchanged from IAP |  | Management control | Partial pass | Presence of manganese in source water is outside of management control, however sedimentation build up in networks may be due inadequate historical flushing regimes
Best option for customers | Pass | South West Water now identifies that it has selected mains for replacement based on likelihood and consequence of failure together with those that are difficult to flush due, for example, to tuberculation [supporting information P41]. We note that there are DWI Regulation 28 Improvement notices for distribution zones ZC5, ZC7 and ZC9 and that schemes to reduce Manganese concentrations from Restormel and St Cleer WTWs are included in the raw water deterioration enhancement programme [Annex P11 & P35]. We note that in zones where Manganese levels entering supply are to be reduced mains cleaning and flushing are required to complete the reduction of taste odour colour complaints. | Securing Cost efficiency - supporting informationvfinal DWI AnnexAvfinal | Best option for customers | Pass | As at IAP. No change in our assessment. |  | Best option for customers | Pass | SWB states it "lags the industry in our south west region. Our targets represent a 50% improvement from our 2016 performance, and will ensure our performance is better than the industry average. Our analysis of costs and benefits shows that this is cost beneficial." [Table Commentary P9] *Proposed programme of work for T,O &C had high levels of customer support [delivering outcomes P26] *Plan not tested for WTP but is limited to those that are cost beneficial based on triangulated values for improving quality & Aesthetics [Delivering outcomes P47] * The 2020-25 £7.800m programme includes targeted mains replacements, network management, flushing and improvements in the control of iron and manganese to the tap.[Table Commentary P263] * Distribution Network - continuous optimisation of treatment processes + DMA flushing £2.1m | Table Commentary P9 & P263 Delivering Outcomes P26 & P47 DWI Letter of Support for process optimisation and DMA flushing Regulation 28 notice
Robustness and efficiency of costs | Partial pass | At IAP we applied 20% challenge to the £5.7m sought for mains replacement and passed £4.56m. The challenge was applied as "that the full level of mains replacement proposed can be justified as the company's assumption of how much will need replacing due to ineffective flushing is not clearly set out". We passed the entire £2.1m sought for process optimisation and flushing. At final determination we find no new WS2 submission, however the company makes representation for its programme of mains replacement [supporting information SWB.DD.CA6 P41]. South West Water identifies that it has developed models to estimate the costs of the programme of rehabilitation work. The company provides an example that mains flushing in St. Thomas Exeter water quality zone [ZE9] has been found to be ineffective and that the network in the location is also subject to DWI notice. It provides a costed schedule of the mains it has identified for replacement in the area, value £1.473m, [supporting information P43] as an example, however complete schedules are not provided. We now accept the costs of the proposed programme of mains replacement. | Securing Cost efficiency - supporting informationvfinal | Robustness and efficiency of costs | Fail | Capex: We have not identified any new evidence and retain our assessment from IAP. Opex: There is no opex spend identified on this enhancement line. |  | Robustness and efficiency of costs | Fail | SWB demonstrates its approach to costing. "We engaged industry experts, Chandlers KBS and Aqua Consultants, to undertake a review of our cost models and data compared to peers within the industry." They concluded that, based on the comparative information available, South West Water models are competitive with a good indication that the models are efficient and with limited scope for further efficiencies at the business planning stage..[Securing cost efficiency P31] Independent report not found, inclusion of independent reports would support claims for cost efficiency. Mains replacement - £5.7m is a material level of spend. We find insufficient evidence of a build up of this expenditure to be able to calculate a unit rate or identify target locations. Only work in areas subject to TOC issues may be charged to this line. DWI letters gives support if flushing is found to be ineffective. However, it is not clear that the full level of mains replacement proposed can be justified as the company's assumption of how much will need replacing due to ineffective flushing is not clearly set out. As the scope and length of mains to be replaced is not defined we apply a 20% challenge to this part of the scheme and allow £ 4.56m. We accept process optimisation & flushing works and allow the £2.1m that SWB propose for this. To give a total allowance of £6.66m. | BP Securing Cost Efficiency P31
Customer protection | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Customer protection | Pass | As at IAP. No change in our assessment. |  | Customer protection | Pass | SWB proposes an ODI with out performance payment and under performance penalty [Delivering Outcomes P49]. Customers are protected by DWI Notices under Regulation 28 to mitigate risks to wholesomeness of water. SWB states that the Plan is stress tested to ensure that it is deliverable [Delivering outcomes P45]. | [BP doc Delivering Outcomes] DWI Letters of support
Affordability | N/A |  |  | Affordability | N/A |  |  | Affordability | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | Board assurance | N/A

## Deep dive_WSH
Deep dive sheet - Welsh Water | [10 empty] | Summary at DD - Taste, odour, colour line |  |  |  | Summary at DD - Network water quality freeform line | [6 empty] | Data in Blue is from 5.8I Acceptability of Water Service Improvement P18/P19
[22 empty] | Zonal Work | Budget £m | Budget Mgmt. fees redistributed | Comment | Ofwat View of allowance £m | Comment
Summary | [10 empty] | Summary |  |  |  | Assessment | [6 empty] | Zonal Studies Strategy
Company | WSH | [9 empty] | Company | WSH |  |  | Assessor name | PM | [5 empty] | Mains Abandonment | 0.62 | 0.65288 | mgmt. fees redistributed | 0.65288 |  | Mains replacement unit cost check
Control | Wholesale water | [9 empty] | Control | Wholesale water |  |  | Company | WSH | [5 empty] | Mains Cleaning | 24.21 | 25.494 | mgmt. fees redistributed | 3.1715 | proportion allowed - calculation below | Length Replaced [km] | Unit cost £m/km
Totex carried through deep dive AMP7 (£m) | 27.219 | We reallocate the Network Water Quality freeform line to this line. This gives a total requested of £117.931m for final determination, the same as for draft determination. This comprises £27.179m taste odour colour capex, £0.04m taste odour colour opex and £90.712m network water quality capex. | [8 empty] | Totex carried through deep dive AMP7 (£m) | 27.219 |  |  | Control | Wholesale water | [5 empty] | Mains Renewal | 95.28 | 100.3331 | mgmt. fees redistributed | 6.8866 | proportion allowed - calculation below | 420 | 0.23889 | Based on cost including mgmt. but pre-efficiency
Totex assessed within cost adjustment claims (£m) | [10 empty] | Totex assessed within cost adjustment claims (£m) |  |  |  | Totex carried through deep dive AMP7 (£m) | 90.712 | [5 empty] | Mgmt. Fees | 6.37 | 6.7078 |  | 0.56805 | pro rata
Totex assessed within deep dive (£m) | 27.219 | [9 empty] | Totex assessed within deep dive (£m) | 27.219 |  |  | Totex assessed within cost adjustment claims (£m) | 0 | No associated CAC |  |  |  |  | Zonal Work Sub Total | 126.48 | 133.1878 |  | 11.279
Totex allowance from cost adjustment claims (£m) | [10 empty] | Totex allowance from cost adjustment claims (£m) |  |  |  | Totex assessed within deep dive (£m) | 90.712
Totex allowance from deep dive (£m) | 96.8656 | At draft determination we set a combined allowance for expenditure to improve acceptability of water to customers. The combined allowance considered the water acceptability cost adjustment claim which we allocated to this taste, odour and colour enhancement line together with the network water quality freeform line. Accordingly, to reflect this combined approach we now present both the taste odour colour (TOC) and the network water quality (NWQ) within this feeder model. Dŵr Cymru represented on the network water quality, WSH.DD.CE.3, and not on the taste odour colour. We provide our assessment of the network water quality representation in columns B to F. We provide our assessments of allowances for taste odour colour and network water qaulity in their component elements in columns J to P and this results in a combined increased allowance following the company’s network water quality representation. We continue to intervene to set a more stretching customer acceptability performance commitment target. | [8 empty] | Totex allowance from deep dive (£m) | 27.219 | We consider this line together with the network water quality (new legal obligations) free form line and apply a programme level cost challenge to set the combined allowance. |  | Totex allowance from cost adjustment claims (£m) | 0 | No associated CAC
Ofwat view of totex allowance for AMP7 (£m) | 96.8656 | [9 empty] | Ofwat view of totex allowance for AMP7 (£m) | 27.219 |  |  | Totex allowance from deep dive (£m) | 32 | [5 empty] | Other Activities zonal
[15 empty] | Ofwat view of totex allowance for AMP7 (£m) | 32 | Dŵr Cymru proposes significant enhancement expenditure to improve acceptability of water to customers (a cost adjustment claim which we allocated to taste odour and colour enhancement lines) and network water quality (freeform). We acknowledge that the company’s performance needs to improve in this area but consider this to be covered by the implicit base allowance. We make a combined partial allowance for the two related investments that comprise this programme, apply a programme level cost challenge and intervene to set a more stretching customer acceptability performance commitment target. |  |  |  |  | Hydrant capping (urban 10,000) | 0.14 | 0.14 |  |  | Base
Assessment | [10 empty] | Assessment |  |  |  | Proportion in water N+ | 100% | All totex expenditure included in water network plus in table WS2 |  |  |  |  | Dead end cleansing (top ten zones care plans @ £300k) | 3.18 | 3.18 |  |  | Base
Assessment gates |  |  | References | DD Ref | Description | DD Post WSH efficiency | Design Flow [Ml/d] | Cost / Mld | Scheme Level Assessment | Allowance - pre company efficiency challenge | Assessment gates |  |  | References | Deep dive company efficiency challenge | 5% |  |  | IAP Assessment |  | References | Mains conditioning (~ five locations) | 1.71 | 1.71 |  |  | Base
Need for investment | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | DD table WS WN WR Commentary P12 | Worst Served Customers | 3.056 | n/a | n/a | Dŵr Cymru identified that these schemes are to resolve persistent TOC issues. The company outlines the cluster analysis process followed to identify the 13 clusters of worst served customers where it intends to resolve TOC complaints [DD document 2.15.WSH.CE.A1 P19]. These are identified together with the selected renewal / cleanse options and unit costs of £300/m for renewal and £30/m to cleanse pipework [2.15.WSH.CE A1 P19-20]. The company provides cost/customer, property and complaint data but not projected schemes impact on TOC contacts / 1000 customers. Dŵr Cymru notes that carrying out interventions for these customers would not be cost beneficial in many cases [B2.15 P19]. As we find no cost benefit assessment and insufficient evidence of the impact on TOC contact rates we apply a 20% scope challenge. | 2.4448 | Need for investment | Partial pass | In the April business plan the schemes allocated to this line are * acceptability of water worst served customers, * Zonal modelling studies, * Acceptability strategy improvement projects and * WTWs manganese improvements. [B3.A4. P12]. In its September business plan Welsh Water included investment to deliver new network water quality projects in this line. For the April plan submission the company allocated this to the network water quality (new Legal obligations) free form enhancement line. As investments to both lines are to address both taste, odour and colour we assess them together and set a combined allowance. We assess those elements of the investment that Welsh Water allocated to the taste, odour and colour line in its April plan in this model. WTW Mn improvements: Welsh Water presents evidence of high concentrations of manganese [Mn] in its raw water sources [B2.15.WSH.CE.A1 P23- 24] and that this is a cause for TOC complaints [B2.15.WSH.CE.A1 P5]. The company states that following completion of DWI mandated programme of work to the network reduction of manganese [Mn] levels in treated water would remove the source of future taste, odour, colour [TOC] complaints [B2.15.WSH.CE.A1 P9]. We note that process optimisation is required at some works in this programme in order to comply with DWI notices [DWI Notices B.16]. We accept this justification of schemes at those sites. We find no evidence that Mn in the distribution input from the other WTW fails PCVs. However we note the correlation of high levels of Mn with TOC complaints [B2.15 P10]. The company estimate the reduction in TOC complaints from this programme in the period 2020 -25 as 0.104 /1000 population [B2.15 P9]. Zonal Studies: In its September business plan Welsh Water justified zonal modelling studies as the means of identifying causes of poor performance and targeting investment [5.8I P15]. An understanding of network assets is necessary for normal operations, it is a base service activity. Worst Served Customers: Welsh Water justify the worst served customers programme on the basis that the company has a duty of care to ensure that all customers receive a satisfactory service even when this may not be cost beneficial. [B2.15.WSH.CE.A1 P19] . Operational Improvements: Welsh Water describe the remaining investment as "enabling activities for operational improvements" [B2.15 P3] , The programme of work is justified as an extension of the work being undertaken 2015-20, and the company estimates that this will reduce TOC complaints by 0.022/1000 customers [B2.15 P9]. At IAP we noted company cost benefit analysis [CBA] undertaken supports a level of performance in the range of 2.0-2.4 contacts per 1000 population, well above the industry standard [5.2 P40]. Welsh Water identify customer contacts for TOC at 2017 as 2.70 [B2.15.WSH.CE.A1 P5]. WSH forecast 2.4 TOC contacts / 1000 customers at 2019-20 and is targeting 2.0 at the end of 2020-25[5.8I P4]. The Ofwat target for TOC complaints is 1.58/1000 customers. The total improvement in TOC complaints identified for this programme is 0.126 /1000 customers. As we find no evidence of the improvements in TOC complaints from the zonal studies and worst served customer programmes we award a partial pass. | Ref B2.15.WSH.CE.A1 Revised Cost Adjustment Claim Acceptability of Water, 1 April 19 B3.A.4 Welsh Water Water Services Table Commentaries WS WN WR April 2019 IAP doc: 5.8I PR19 IC Acceptability of Water Service Improvement | Need for investment | Pass | We have identified the 17 Drinking Water Inspectorate (DWI) notices presented in full in the company's Appendix 1. We have reviewed the example documents for completion of milestone 2 from the AMP6 programme for DWR3534. We pass the need for investment based on the legal obligations that Dŵr Cymru is under - the Water Supply (Water Quality) Regulations 2010, Regulation 29(4) - for risks associated with discolouration and associated customer acceptability due to the condition and operation of the network. | p3, B2.16.WSH.CE.A1 Network water quality - new legal obligations DWI Notice, 28th March 2017, for Hereford North, DWR3534 Milestone report Letter from DWI, 27th March 2019, for Hereford North, Notice DWR3534 | Pass | WSH proposes a programme of zonal studies for reducing Mn supplied via the distribution system to achieve compliance and reduce TOC customer contacts. We find DWI notices for TOC network studies with completion dates in AMP7. [Ref: 5.8I] However, the scope of work proposed by the company includes WTW process upgrades where we can find no evidence of DWI support. The company states, "During AMP6 we worked with the DWI to improve this performance, resulting in the DWI issuing improvement notices for 32 of our 83 water quality zones. The notices are provided in Supporting document 5.8I.3. [5.81 p6] ..., of which 14 are being addressed in AMP6 with the remainder being dealt with in AMP7." [Ref 5.2 p41] The company stated "Zonal Studies will continue in AMP7 and we will complete interventions in an additional 17 zones which have legal notices for improvement. This will include the replacement of 420 kilometres of water mains along with mains cleansing and rehabilitation, and the redesign of the supply network to maximise future supply resilience for customers" [BP pp65-66]. WSH submitted a cost adjustment claim ref WSH-WN602001 "Acceptability of Water Service Improvement". We fail that claim as WSH did not identify a difference from other companies and therefore should not be allowed money to catch up. However we recognise that we should set an allowance for appropriate enhancement activity. | DWI letters Acceptability - Commend for Support; Merthyr T&O - Commend for support. DWI Notices referenced in 5.81.3 5.2 p41 BP CAC WSH-WN602001 | Customer information on domestic plumbing and taste and odour issues £0.32 m | 0.32 | 0.32 |  |  | Base
Need for adjustment | Partial pass | Dŵr Cymru notes that expenditure was £30m over the 2010 to 2015 period, nominally as per the PR09 allowance. This included 3 specific trunk mains rehabilitation schemes, zonal studies and maintenance strategy expenditure. We note that contacts rose to 3.5 contacts/1,000 population during this 2010-15 period. During the 2015 to 2020 period, expenditure is forecast to be £130m, made up of the company's PR14 allowance of £70m and an extra £60m of Board-approved expenditure on water acceptability. This increased activity is across 13 water quality zones through various work streams. We note that during the 2015 to 2020 period contacts/1,000 population reduced and are predicted to reduce further to 2.40 at the end of the 2015 to 2020 period. During the 2020 to 2025 period, expenditure is forecast to be £90.7m. This increased activity is across 17 water quality zones through various work streams. We note that Dŵr Cymru predict the 2020 - 2025 period contacts to reduce to 2.00 contacts/1,000 population by the end of the period in 2024-25. We note the recent increased activity by Dŵr Cymru is to address improvements in network water quality and to meet statutory water quality obligations. We note that Dŵr Cymru is forecasting less than upper quartile percentage improvement in its business plan and therefore maintain our DD approach. | PR19 DD WSH.DD.CE.3 Network water quality - new legal obligations B2.15.WSH.CE.A1 Cost Adjustment Claim AOW WSH.DD.OC.1 Performance Commitments |  | Zonal Studies & models [5.8I P18] | 2.253 | n/a | n/a | The work is identified as hydraulic & deterioration modelling plus desktop assessments - to predict current and future performance of network. We note that Dŵr Cymru split the cost of this work equally between botex and enhancement. [IAP Doc 5.8L P2]. We find no reference to the scope and costs of these studies in DD cost claim document ref B2.15, however we note that the programme is included in WS2 line 4 [DD table commentary B3.A4 P12] is equal to that presented in table WN6 for the cost claim. We consider that an understanding of network operation is normal operation and not an enhancement activity and make no allowance for these costs. | 0 | Need for adjustment | N/A |  |  | Need for adjustment | Partial pass | Dŵr Cymru claims it not to be appropriate to include expenditure required to deliver outputs to meet legally binding DWI notices in the taste, odour and colour enhancement line and has presented the costs separately as an enhancement freeform line. This separation is useful at the programme level. However, we consider these costs to be part of base expenditure to maintain assets to meet existing DWI standards. We acknowledge that the company's performance needs to improve and make a combined partial allowance for the two related investments across the programme. Allowing the full amount in the Taste Odour and Colour enhancement line and the residual allowance against this freeform line. | p1, B2.16.WSH.CE.A1 Network water quality - new legal obligations | N/A |  |  | Other Activities subtotal | 5.35 | 5.35
Management control | Partial pass | As explained in our DD assessment we consider that part of current position has been partially influenced through management control. In its representation the company considers that our draft determination was based on the assumption that Dŵr Cymru failed to apply management control and invest previously to address taste odour and colour complaints at the same level as the rest of the sector. To address this, the company argues that over the last 10 years it has spent considerably more than it has been allowed in final determinations on water network improvements, noting that the company’s Board has sanctioned significantly more expenditure in the 2015 to 2020 period than was allowed for in PR14. Dŵr Cymru argues this demonstrates in very practical terms that the company considers this investment to be essential on behalf of its customers. It also adds that the fact that the investment is encapsulated in DWI legal notices demonstrates that it agrees with this assessment. We acknowledge the extra approved expenditure made by the Dŵr Cymru Board in the 2015 to 2020 period to improve performance. We have carefully considered this action and have adopted an 'in the round' approach to setting this allowance with Drinking Water Inspectorate support and UQ %improvement rate on behalf of customers during the 2020 to 2025 period. We continue to apply a partial pass recognising the 2015 to 2020 period expenditure, but continue to challenge management control to deliver service experienced across the industry. | PR19 DD WSH.DD.CE.3 Network water quality - new legal obligations WSH.DD.OC.1 Performance Commitments |  | Other Activities subtotal | 5.033 | n/a | n/a | The company’s initial business plan indicated individual schemes within the other activities programme of work [5.8I P19], these schemes included one for fitting of hydrant caps. We cannot find the breakdown of costs by activity. We therefore consider those activities to be covered by base operating costs. At draft determination we note that the scope of work to be undertaken in this programme is different from that at IAP. We find no breakdown of the cost by activity. We consider activities now identified to be base operating costs [B2.15 P16-18]. | 0 | Management control | Fail | Welsh Water provides evidence that it has high levels of Mn in its raw water [B2.15.WSH.CE.A1 P23-24]. The company identifies that it already uses mains flushing and the installation of inline filters to address TOC complaints [B2.15.WSH.CE.A1 P20]. This identifies that management action can be taken to resolve the issue of Mn in the network. Welsh Water propose process optimisation to reduce Mn levels in treated waters from some WTWs [B2.15.WSH.CE.A1 P 26] It is unclear why process optimisation has not previously been completed. In its September business plan the company identified weak performance relative to the rest of the industry [5.2 P41]. This is also evidenced in the chart in B2.15.WSH.CE.A1 P6. We note that Welsh Water identifies Mn levels in the network as a cause of TOC complaints and that Yorkshire Water and United Utilities have similar proportions of water supplied from impounding reservoirs but achieve lower levels of Mn at customers taps [B2.15.WSH.CE.A1 P6]. Allowances have been made in the past for renovating company networks and addressing customer acceptability issues however as Welsh Water acknowledges performance remains weak. Although the geology of the company's operational area is outside of management control. We consider that Welsh Water has not applied sufficient control to address the challenges presented by this. | B2.15.WSH.CE.A1 Cost Adjustment Claim AOW Ref 5.2 PR19 Performance Commitments | Management control | Partial pass | We have identified that Dŵr Cymru intervention costs have been built bottom up from individual schemes identified in each zonal study and that the preferred solution has been selected using a cost benefit methodology. We note that through discussions with South West Water (SWB) both similarities (manganese levels in reservoir sources, source to tap approach to minimise manganese impacts, conditioning of trunk mains and improvement notices with DWI) and differences (SWB had a larger investment programme, that focused on relining trunk mains, high summer demand tourism vs. industrial decline) have been identified. We also note that Dŵr Cymru has provided additional information to the issues raised by our IAP assessments, and whilst this is helpful, at a programme level there is still insufficient evidence to demonstrate that these decisions are considered outside of management control. Dŵr Cymru argues that in AMP3 and 4 the mains replacement programme was subject to additional cost pressures that arose due to geographical programme deviation (more urban vs. rural) and original 50/50 split of reline/renew. This delivery budget constraint meant that smaller diameter pipework were replaced, increasing water quality compliance performance but leaving high cost, low output, predominately unlined ferrous pipes to deteriorate. This was an apparent difference in approach at South West Water who relined significant lengths of trunk mains, however, we have been unable to identify any bespoke evidence presented by Dŵr Cymru regarding the relative size of mains relined and wider management decisions and therefore apply a partial pass. | p5, B2.16.WSH.CE.A1 Network water quality - new legal obligations Appendix 3 - Issues raised in Ofwat's IAP feedback | Partial pass | WSH identifies soft water with high levels of manganese together with a high proportion of unlined iron pipes as the cause of high TOC complaints. [Ref: 5.81 p5] It states that this is outside of management control, however sedimentation build-up in networks may be due inadequate historical flushing regimes. The company states "Our performance on this measure has been weak compared with the rest of the industry. In 2017/18 our 2.79 contacts per 1,000 population served compared with an estimated upper quartile performance across the sector of 0.77. This represents significant progress from the figure of 3.53 in 2014/15, and we are projecting further improvement to 2.4 by the end of AMP6, but we are already paying financial penalties for missing our AMP6 FD targets and expect to continue to do so up to the end of the period." [Ref: 5.2 p41] This suggests that WSH was awarded enhancement spend in 2020-2025 but is failing to deliver the expected benefit. | Ref 5.2 PR19 Performance Commitments | Total all zonal activities | 131.83 |  |  | 11.279 | Total allowed all zonal activities
Best option for customers | Pass | Dŵr Cymru notes that discolouration raises some modest concerns for customers and the support for significant investment to achieve further improvements is limited. From the information presented there was no educational content provided on industry comparisons to elicit customer views that highlights the poor performance of Dŵr Cymru relative to the service experienced across the industry. We intervene for the benefit of customers to make upper quartile percentage improvements (calculated as 34% from the 2019-20 position to the 2024-25 on industry level data). This results in 1.58 contacts/1,000 population for Dŵr Cymru based on its 2019-20 forecast of 2.40. We set a linear profile for 2020-2025 to get the company to the 1.58 target reflecting the upper quartile percentage improvement by 2024-25. We are continuing to intervene for the benefit of customers to make UQ %improvement (calculated as 34% from 2019-20 position to 2024-25 on industry level data) to make improvements in the service provided by Dŵr Cymru towards those experienced by customers across the industry. We therefore pass this gate with the stretching target. | p16 to 20 IAP Response - B2.2.WSH.OC | DD Scheme Level costs [B2.15.WSH.CE.A1 P12-15]. | WTW Improvements | 3.42 | 34 | 0.10059 | Alaw Dŵr Cymru provides evidence that on occasion Mn levels in the final works output exceed 20% of PCV [Query WSH-DD-CA-003-PR19 Report Alaw WTW]. However the Mn concentration data provided in information provided for another scheme identifies 95% Mn levels below 10 ug/l [CA 003 Cefn Llan P2]. WSH identify a TOC contact rate of 9/1000 customers approx. [B2.15 P10]. Evidence of optioneering provided in [CA-003 Alaw]. This report identifies Option 1 Mn removal on RGF as having lowest costs capex cost to client £0.883m, 40yr totex £2.196m. Option 2 which comprises Replace RGFs with GAC and convert ex GAC to Mn oxidation filters costed at capex - £3.705m and 40yr totex - 4.725m. Option 2 is presented as the selected option in B2.15 P12. We find insufficient evidence to justify the selected option and make allowance for the least cost option identified in the optioneering report. | 0.883 | Best option for customers | Partial pass | WTW Mn Improvements: TOC complaints are associated with Mn levels, the company provides evidence of high levels of Mn at customers taps and TOC complaints. Reduction of Mn in water entering supply address a root cause of TOC complaint. Welsh Water provides evidence that it is has followed a process to identify WTWs for engineering solutions and process optimisation based on Mn levels entering supply and TOC complaints [B2.15.WSH.CE.A1 P10 11]. We accept this overall approach but comment on individual schemes: • Alaw: Welsh Water provides evidence of optioneering [CA-003 Alaw]. This report identifies Option 1 Mn removal on RGF as having lowest costs however Option 2 is presented as the selected option in B2.15 P12. We find insufficient evidence to justify the selected option. • Cefn Dryscoed: We note that the CA 0003 report identifies de-stratification as least cost but discounts the option because of insufficient evidence of that stratification was occurring in the reservoir. Welsh Water identifies that the works is currently performing well but not fully in line with the company’s specifications, however it identifies the possibility of a deterioration in time. We find insufficient justification to discount the do nothing option." • Alwen: Welsh Water selects the installation of de-stratification process in the impounding reservoir as well as minor process improvements and optimisation over the discounted do nothing option and construction of a new process at the works. [B2.15 P13]. We note that Mn concentrations in the final water may have increased consequent to the change in coagulant, however further evidence is required to demonstrate current 95% ile concentrations. It is unclear if there is a need to continue with the use of ferric coagulant. Also it is unclear why the company has selected an option that was discounted in the optioneering report. " • Pen y Cefn: The optioneering report discounts do nothing [CA 0003 P16] none of the costed options are identified as cost beneficial. Further evidence of Mn concentrations in output water is required to support the discounting of do nothing." • Cefn Llan: We note that the optioneering report proposes a different option with a marginally lower costs [CA 0003 Cefn Llan P4 & 6] than that selected in the CAC report [B2.15 P14] but accept the reasoning presented as the difference is less than 1%." • Pendine: The CAC document [B2.15 P14] selects an option similar in scope to Option 2 above. The reason for option selection lacks clarity and we find no evidence that provides reason for the increase in cost compared to that in the optioneering report. Zonal modelling studies: Studies may be used to identify areas of performance deficiency and target investment requirements. Worst served customers: Welsh Water identifies the numbers of properties and complaints in each cluster of worst served customers proposed for remedial work. However we find no evidence of the projected impact on TOC contacts /1000 customers. We note that the company identifies that some schemes may not be cost beneficial [B2.15.WSH.CE.A1 P19]. Acceptability strategy improvement projects: The scope of this programme appears different to that proposed in the company's September business plan. We find no evidence of CBA in the April submission. Summary: We find evidence that elements of the programme present the best option for customers assess this as a partial pass. | PR19 Water Resources BP p24 Ref 5.2 PR19 Performance Commitments Ref 5.81 PR19 Acceptability of Water Service Improvement | Best option for customers | Pass | We have identified the wider benefits presented by Dŵr Cymru with the network water quality improvements for the Maerdy Porth case study. The example given is the Rhondda Fach Water Resilient Pilot Project, that ran concurrently with the network water quality improvements. The benefits noted include reducing debt burden through HelpUsocial tariff, engagement with schools and communities on water efficiency, stakeholder engagement and apprenticeship programmes within the local community. | p6, B2.16.WSH.CE.A1 Network water quality - new legal obligations | Partial pass | WSH is also using catchment management [WR BP p24]. The company states "discolouration events are strongly linked to the removal of biofilms from the surface of pipes. These biofilms can acquire ‘colour’ from both manganese and particulates that result from the soft water corrosion of unlined cast iron pipes." [Ref: 5.81 p5] WSH also identifies that although discolouration does raise some modest concerns for customers, the support for significant investment to achieve further improvements in this measure is limited. Further, cost benefit analysis supports a level of performance in the range of 2.0 – 2.4 contacts per 1,000 population, well above the current industry standard. [Ref: 5.2 p40] WSH is setting a target at the upper end of the range supported by customers. Cleaning and mains replacement continues work from 2020 -2025 however failure to achieve targets in 2020 -2025 identifies that a change in approach is required. WSH identifies four options for Acceptability of Water Service improvement and have selected "integrated intervention programme with enhancement......main benefit of our chosen solution is that it achieves an improvement for each of the investment areas at the lowest total expenditure (totex) option to meet our water quality needs." [5.8I p17] WSH provides evidence that it has targeted work at WTWs appropriately. "As we now understand how even very low levels of manganese can contribute to discolouration, we will build on our manganese removal trials...... to implement manganese reduction schemes at five water treatment works through a £16.5 million investment. Sites have been chosen based on criteria that identify sites with the highest manganese concentration, together with elevated customer contacts...." [BP pp65-66] | PR19 Water Resources BP p24 Ref 5.2 PR19 Performance Commitments Ref 5.81 PR19 Acceptability of Water Service Improvement | Total Allocated to enhancement/CAC [= total from table on P18 5.8I | 107.62
Robustness and efficiency of costs | Partial pass | In its representation, Dŵr Cymru provides limited network water quality improvement scheme details for the 2015 to 2020 period to demonstrate efficiency of costs. For this reason, we conduct a top down assessment of these costs. We note that unit rates used to cost the programme of works are derived from Dŵr Cymru’s unit cost data base. We continue to challenge the level of uncertainty surrounding the solutions and costings of the schemes. For this reason we maintain a partial pass and apply the company deep dive efficiency challenge. | PR19 DD WSH.DD.CE3 Network water quality (Legal obligations), Section 2.2 |  |  | 1.71 | 25 | 0.0684 | Cefn Dryscoed The company provide evidence that on occasion Mn levels in the final works output exceed 20% of PCV [WSH-DD-CA-003-PR19 Report Cefn Dryscoed WTW P7], however, the Mn concentration data provided for another scheme identifies 95% levels below 10 ug/l [CA 003 Cefn Llan P2]. Dŵr Cymru identifies TOC contact rate of 8.3/1000 approx. [B2.15 P10]. The company selects the installation of de-stratification process in impounding reservoir as well as minor process improvements and optimisation [B2.15 P13]. We note that the CA 0003 report identifies de-stratification as least cost but discounts the option because of insufficient evidence of the fact that stratification was occurring in the reservoir. We find no costing of the de stratification in the CA 003 report. Additionally ,in discounting the 'do nothing' option [CA 003 report P8] Dŵr Cymru identifies that the works is currently performing well but not fully in line with the company's specifications and it identifies the possibility of a deterioration in time. As the works is currently performing well we find insufficient justification to discount the do nothing option and therefore make no allowance for this scheme. | 0 | Robustness and efficiency of costs | Partial pass | At IAP this programme of works were part of Cost Adjustment Claim WSH-WN602001 (value £118.07m) 'Acceptability of Water Service Improvement'. At DD the IAP programme has been split between this TOC line and a new freeform line. Capex: * WTW Mn improvement: Welsh Water has provided scheme level costs for these works. The company states that only those costs not covered by the DWI notices are included in the CAC and thus this enhancement line. [B3.A4 P112]. However we note that process optimisation at WTWs identified in the DWI notices has been allocated to this line. We consider each scheme individually and note the following: • Cefn Dryscoed: We find no costing of the selected de stratification option in the CA 003 report. • Pen y Cefn: With the 40 year totex least cost option is identified as having a capex of £0.185k [CA 0053 P18-19]. We find no evidence to explain the increase in scheme capex from optioneering report to cost claim document. • Pendine WTW: We find no evidence to provides reason for the increase in cost compared to from optioneering report to cost claim document. . * Zonal studies We consider that an understanding of network operation is normal operation and not an enhancement activity. * Worst Served Customers: The company has provided scheme level costs of these. * Operational Improvements: We find no scheme level costs or outputs for these projects. Opex: At both IAP and DD Welsh Water seeks £0.040m water treatment opex. At IAP WSH states "The spend profile has been targeted to achieve improvements at the WTW in particular during the first three years of AMP7. Linked with this programme of work is line B44 which includes an opex impact for these projects of £0.008m." [IAP Table commentary P 12]. We consider the annual opex spend of £0.008m is to maintain the performance of the enhanced WTWs. Our modelling of treatment costs includes a WTW complexity variable. Therefore operational cost of the enhanced works is included in our base modelled costs. Summary: We find insufficient detail and justification of some scheme costs. We make allowance by considering this line together with the Network water quality (new legal obligations). The allowance allocated to this line is £27.219m. | Deep Dive tab, BP tables 5.8I IAP: 1.2 Water services table commentaries | Robustness and efficiency of costs | Partial pass | We note that costs presented are estimates based on the zonal studies and not specific site studies. Dŵr Cymru acknowledges there is a 'small element of uncertainty' until specific programme of works are agreed with the DWI. Dŵr Cymru commissioned Mott MacDonald to provide assurance on the construction costs in the Unit Cost Database used in the PR19 investment programme. We note that Mott MacDonald concluded that the unit costs presented by Dŵr Cymru were aligned to the dataset of industry costs held by Mott MacDonald. Whilst this provides some high level assurance that costs are broadly aligned with the industry, it does not provide detailed examples or potential opportunities to reduce costs further in line with other initiatives mentioned. We could not identify where the implicit allowance has been removed from the programme of works costs. No detailed cost breakdown example has been identified. DWR3534 - Hereford North is presented, but provides no detail of the cost build-ups. | p5, B2.16.WSH.CE.A1 Network water quality - new legal obligations p11, 3.6 PR19 Costs efficiency, benchmarking and recovery WSH, Sept 18 | Fail | Costs are presented in Cost Adjustment Claim WSH-WN602001 (value £118.07m) 'Acceptability of Water Service Improvement'. The CAC includes £20.14m [pre-efficiency] for Mn WTW improvements and £107.62m for Zonal study interventions [which include mains cleaning and replacement]. The costs of the programme are analysed in Columns K-S of this Deep Dive tab. Mains Replacement: Our analysis of BoN1200 data identifies that WSH plans a total of 424km of mains renewals in AMP7. This is 1.89% of water main length, close to the industry average of 1.85% but significantly above industry median of 1.72%. We select SWB as a comparator for mains replacement. SWB has similar geology and has a programme of mains cleaning and replacement driven by TOC. Our allowance for SWB's cleaning and renewal programme is £6.66m. On this evidence we consider that WSH has previously failed to invest in mains replacement consequent to asset deterioration and that the proposed programme is driven by WSH's need to catch up with the rest of the industry. We also note that nearly all mains replacement [420 vs. 424km company-wide] is in zones designated by the TOC programme. We calculate the allowance based on the programme that SWB propose. WSH claim £97m for mains cleaning and replacement work. We allow £10m. Other schemes: * WSH present insufficient of evidence of the scope of work at WTWs or that full optioneering has been completed for these schemes. Therefore, we apply a 20% to the submitted costs for these schemes. * We accept the costs of the zonal studies. * We find insufficient evidence that the worst served customers work is driven by TOC. We apply a 20% challenge to these costs. WSH request a£25.15 for these other schemes we allow £18.5m. | Deep Dive tab, BP tables 5.8I | Apply WSH Efficiency challenge [calculated from data 5.8I P24] | 9.75% |  |  | 11.47% | apply revised efficiency challenge [see cell L31:M31]
Customer protection | Pass | We note that Dŵr Cymru forecasts less than UQ %improvement in its business plan. We maintain our DD approach and are intervening for the benefit of customers to make UQ %improvement (calculated as 34% from 2019-20 position to 2024-25 on industry level data). This results in 1.58 contacts/1,000 population for Dŵr Cymru based on its 2019-20 forecast of 2.40. We set a linear profile for 2020-25 to get company to 1.58 UQ %improvement by 2024-25. We note that outcome delivery incentives are attached to Wt3 Acceptability of drinking water to protect customers by returning any allowed totex that remains unspent at the end of the 2020 to 2025 period. | WSH.DD.OC.1 Performance Commitments B2.16.WSH.CE.A1 Network water quality - new legal obligations |  |  | 0.82 | 50 | 0.0164 | Alwen Welsh Water provide evidence that on occasion Mn levels in the final works output have exceeded 20% of PCV[WSH-DD-CA-003-PR19 Report Alwen WTW]], however, the Mn concentration data provided for another scheme identifies 95% levels are approximately 2 ug/l [CA 003 Cefn Llan P2]. The company also identify a TOC contact rate of 3.5/1000 approx. [B2.15 P10]. WSH select the Installation of de-stratification process in impounding reservoir as well as minor process improvements and optimisation over the discounted do nothing option and construction of a new process at the works. [B2.15 P13]. From the WSH-DD-CA-003-PR19 Report Alwen WTW report we note that: * reservoir stratification does occur but because manganese in the raw water is present in soluble form all year round Dŵr Cymru concludes that a de-stratification system would be unlikely to assist with manganese removal [ P9]. * the increase in Mn levels in final treated water is attributed to a change in coagulant being used driven by the need to improve organics removal and reduce THM formation. The report identified the least cost option as conversion of existing RGF's to include manganese removal [Option 5 Capex £7.287m]. We note that Mn concentrations in the final water may have increased consequent to the change to ferric coagulant , however further evidence is required to demonstrate current 95% ile concentrations. It is unclear if there is a need to continue with the use of ferric coagulant. We find no evidence to explain why the reversion of the coagulant from ferric to that used previously would not resolve the issue of Mn concentrations in the water supplied from the site and make no allowance for this scheme. | 0 | Customer protection | Pass | Failure to implement the Manganese reduction from WTWs will present risk of non compliance with DWI notices. | IAP doc: App 5.5 PR19 Outcome Delivery Incentives | Customer protection | Pass | Dŵr Cymru proposes a customer protection outcome delivery incentive (ODI). We consider that customers appear to be adequately protected with the inclusion of this new performance commitment, 'Delivery of our water network improvement programme'. We note that the totex value spent against the programme is to improve the performance of water networks in response to the DWI notices and the intention to return in full to customers any allowed totex that remains unspent at the end of AMP7. Dŵr Cymru is proposing an improvement to 2.00 contacts per 1,000 population, however to achieve upper quartile (UQ) 34% performance we are intervening to set a stretching improvement of 1.58 per 1,000 population. | p 5, B2.16.WSH.CE.A1 Network water quality - new legal obligations | Partial pass | Customers are protected by DWI letters of support and ODI capped outperformance payments and collared penalties [App 5.5 P41]. However, it should be noted that WSH is currently (in 2015-2020) achieving below target performance for TOC [5.2 P41]. See Management Control above. | App 5.5 5.2 p41 | Total all zonal activities post efficiency challenge | 97.1269 |  |  | 9.9849
Affordability | N/A |  |  |  |  | 0.33 | 2.5 | 0.132 | Pen y Cefn WSH provide evidence that the 95%ile of final works output is 10 ug/l. However it states that since the WTW was commissioned in 2011 concentrations rarely exceed 10 ug/l [WSH-DD-CA-003-PR19 Report Pen y Cefn WTW P8]. Welsh Water also identifies a high TOC contact rate of 8.6/1000 approx.[B2.15 P10]. The selected option is the retention of aluminium sulphate dosing, conversion of existing RGF filters to catalytic manganese removal media, addition of manganese oxidation upstream of filters using pH correction and chlorine dosing [B2.15 P13]. The optioneering report discounts the do nothing option [Query WSH-DD-CA-003-PR19 Report Pen Y Cefn WTW P16] and none of the costed options are identified as cost beneficial. We note the 40 year totex least cost option is identified as having a capex of £185k [CA 003 Peny Cefn P18-19], which is less than the £0.330m requested. We also note the lack of a site visit in the preparation of the constructability & commissioning issues as unhelpful to confirm efficient costings. We find no evidence to explain the increase in scheme capex from optioneering report to cost claim document. As the company states final water Mn concentrations now rarely exceed 10 ug/l, the adopted action level, we find insufficient justification for the scheme and make no allowance. | 0 | Affordability | N/A |  |  | Affordability | N/A |  |  | N/A
Board assurance | N/A |  |  |  |  | 4.28 | 8.64 | 0.49537 | Cefn Llan The company states that the Mn levels from Cefn Llan WTW are the third highest in the company with a 95th percentile of 16 ug/l. This exceeds the 10 ug/l 20% of PCV. Customer TOC contacts are approximately 3.7/1000 [B2.15 P10]. The company identify that there is no DWI notice for this work [CA 003 P1], however we note that 95percentile levels exceed the 20% of PCV adopted as the standard in the 'network' DWI Notices. We note that the optioneering report proposes a different option with a marginally lower costs [CA 0003 Cefn Llan P4 & 6] than that selected in the CAC report [B2.15 P14] but accept the reasoning presented as the difference is less than 1%. We make allowance for the costs submitted. | 4.28 | Board assurance | N/A |  |  | Board assurance | N/A |  |  | N/A |  |  | Other Works
[6 empty] | 3.26 | 4.8 | 0.67917 | Pendine WTW Welsh Water states that the 99%ile of final works output is over 10 ug/l [CA-003 Pendine P7]. However we note that the 95% value is approximately 8 ug/l [CA 003 Cefn Llan P2]. The optioneering report identifies the three options with the highest benefit to cost ratio [CA 003 Pendine P12 and 21] as: * Option 1 change coagulant to alum or PACI + Ph. correction Capex - £0.644m & WLC - 1.389m * Option 2 ferric coagulant, Mn oxidisation, chlorine & polarite media Capex - £1.324m & WLC - £3.688m * Option 3 New 2nd stage filters, Mn oxidisation, chlorine & polarite media. Capex - £5.481m, WLC £12.964m. The CAC claim [B2.15 P14] selects an option similar in scope to Option 2 above. The reason for option selection lacks clarity and we find no evidence that provides reason for the increase in cost compared to that in the optioneering report. We make allowance for the least cost option as identified in the optioneering report. | 0.644 | [11 empty] | WTW Manganese Improvements [5.8I P18] | 20.14 |  |  | 16.112 | Apply 20% challenge - insufficient detail on scope of works or optioneering
[6 empty] | 3 |  |  | 9 other WTWs - process optimisation. We note that DWI notices require process optimisation at Felindre, Pontsticill, Dolbenmaen , Cwm Dulyn, Cilfor, Nantybwch, Llwynon, Broomy Hill, Llandegfedd, Court Farm, Cwellyn and other works [DD document B2.16.WSH.CE.A1 Network Quality - New legal obligations IAP response]. Given the DWI support for this, we accept these costs. | 3 | [11 empty] | Zonal Studies & models [5.8I P18] | 2.32 |  |  | 2.32 | Accept WSH proposed allocation between botex and enhancement
|  |  |  | DD Scheme Level costs [B2.15.WSH.CE.A1 P12-15]. | Network Water Quality [submitted as freeform line] | 90.712 | n/a |  | In its representation Dŵr Cymru presented evidence of its planned investment to address water acceptability. Investment of £90.7m is planned for 17 zones in the 2020 to 2025 period [B2.16.WSH.CE.A1 P3]. We now conduct a top down assessment of the needs and costs which the following performance commitments are attached: satisfactory delivery of Drinking Water Inspectorate notices for network water quality projects in 17 zones and reduction of acceptability of water complaints to 1.58/1000 population. We now pass this expenditure based on the DWI support, stretching target and cost estimation approach. | 90.712 | [11 empty] | Worst Served Customers | 3.09 |  |  | 2.472 | WSH identifies that it has used cluster analysis to target investment to address the needs of ten clusters worst served customers. However no further detail is provided such as size and location of cluster together with scope of work and options considered - apply a 20% reduction because of these omissions
|  |  |  | Capex Totals |  | 117.874 |  |  | Total - pre company efficiency challenge | 101.9638 | [11 empty] | Apply WSH Efficiency challenge [calculated from data 5.8I P24] | 9.75% |  |  | 11.47% | apply revised efficiency challenge [see cell L31:M31]
|  |  |  | Sub Total - Work originally allocated to line |  | 27.162 |  |  | Sub Total - Work originally allocated to line | 11.2518 | [11 empty] | Sub total Cost Challenge post efficiency | 23.0588 |  |  | 18.5056
|  |  |  | Sub Total - Work at WTWS only |  | 16.82 |  |  | Sub Total - Work originally allocated to line after application of company efficiency challenge | 10.6892
[9 empty] | Sub total - Network water quality after application of company efficiency challenge | 86.1764 | [11 empty] | Grand Total zonal & other = expected requested allowance | 120.1857
[9 empty] | Total Allowance | 96.8656 | [11 empty] | Note: the costs presented in Column M are taken from P18 of document 5.8I Acceptability of Water Service Improvement P18
It is unclear why the total calculated from data in appendix 5.8I differs from that submitted in BP
[22 empty] | Total allowance from BP | 117.891
[22 empty] | We assume that WSH has applied an increased efficiency challenge this is calculated as 1- (117.891/(131.8+20.140+2.32+3.09) | 11.47%
[22 empty] | Ofwat view of allowance after additional efficiency challenge applied | 29.027
Calculation of Allowances for mains cleaning and replacement
[22 empty] | Total Length of mains [km] Average AMP7 | 27923.4
[22 empty] | Total Length of mains SWB Average AMP7 | 18489.6
[22 empty] | Value of mains replacement programme SWB - passed through i.e. includes reduction for lack of definition | 4.56
[22 empty] | Expected value of WSH renewal programme pro rata basis | 6.8866
[22 empty] | Mains cleaning allowed SWB | 2.1
[22 empty] | Expected value of WSH cleaning programme pro rata basis | 3.1715

## Deep dive_YKY
Deep dive sheet - Yorkshire Water |  |  |  | Summary at DD
Summary |  |  |  | Summary
Company | YKY |  |  | Company | YKY
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 17.007 |  |  | Totex carried through deep dive AMP7 (£m) | 17.007
Totex assessed within cost adjustment claims (£m) |  |  |  | Totex assessed within cost adjustment claims (£m)
Totex assessed within deep dive (£m) | 17.007 | For final determination Yorkshire Water seeks the same sums as at draft determination. capex £16.814m and opex £0.193m |  | Totex assessed within deep dive (£m) | 17.007
Totex allowance from cost adjustment claims (£m) |  |  |  | Totex allowance from cost adjustment claims (£m)
Totex allowance from deep dive (£m) | 12.7786 | Our assessment within this line remains as at DD. We make no allowance for opex and apply a 20% challenge to capex. We then apply a company efficiency challenge to set the allowance. |  | Totex allowance from deep dive (£m) | 12.7786 | We find insufficient evidence to justify the division of between base and enhancement costs and apply a 20% challenge to capex. We disallow opex and apply a company specific cost challenge to set the allowance.
Ofwat view of totex allowance for AMP7 (£m) | 12.7786 |  |  | Ofwat view of totex allowance for AMP7 (£m) | 12.7786
Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References | IAP Assessment |  | References
Need for investment | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Need for investment | Pass | Assessment unchanged from IAP. |  | Pass | YKY has DWI letter of support for TOC at Tophill Low WTW. The company demonstrates an increase in TOC complaints and identifies two drivers for this: Algal derived [Geosmin & MIB] and Chlorine derived. It identifies disinfection by-products [DBPs] as the most significant risk. Risks are to both TOC and non compliance with drinking water standards due to RW deterioration. YKY provides evidence of trends in the drivers of TOC issues. | App14a DWI Letter
Need for adjustment | N/A |  |  | Need for adjustment | N/A |  |  | N/A
Management control | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Management control | Pass | Assessment unchanged from IAP. |  | Pass | Changes in raw water that give rise to TOC complaints are largely outside of management control. | App14a part B P4 -5
Best option for customers | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Best option for customers | Pass | In its September BP submission Yorkshire Water did not propose lower whole life cost options because they are less likely to resolve risk. [App 14A Pt B P72]. For the April submission Yorkshire Water provides additional justification for its option selection [CE.A1 P46-48]. We accept this on the basis that the alternate only partially addresses the risks. Following completion of the proposed scheme the outlet flow from Tophill Low works will increase from 61.28Ml/d to 68Ml/d [App 14a Part B Annexes, P65] we note that this increase can deliver resilience and SDB benefits. The company identifies that that customers prioritise clean wholesome water. [App14a P6] and identifies customer support to provide water supply that tastes good [BP App 5a p53]. | IAP Response YK.CE.A1 Securing cost efficiency App14A App5a | Pass | YKY has not proposed lower whole life cost options because they are less likely to resolve risk. [App 14A Pt B P72]. The company identifies that that customers prioritise clean wholesome water. [App14a P6] and customer support to provide water supply that tastes good [BP App 5a p53]. | App14A App5a
Robustness and efficiency of costs | Partial pass | Opex: Yorkshire Water identifies that the effect of increasing treatment complexity is not adequately captured in our base cost models [CE Representation P14 & 51]. Following responses to our draft determinations and additional analysis of company data, we adopt company forecasts for the percentage of water treated in treatment complexity bands 3 to 6 and weighted average water treatment complexity in our modelling of base costs. We do not make an allowance to operate the enhanced treatment processes as part of this assessment. These costs are captured in our modelled base allowance through the treatment complexity variable which is now based on companies’ view of complexity in 2020-25 Capex: The company has not raised substantive issues in its representation and we retain our draft determination assessment for capex regarding this gate. | DD Representation Cost Efficiency | Robustness and efficiency of costs | Partial pass | Capex: In its September BP submission Yorkshire Water sought £ 16.821m and we made an allowance of £10.229m. For the April business plan submission Yorkshire Water identifies a post efficiency scheme capex of £19.00m for the selected option at Tophill Low [CE.A1 P46]. This comprises enhancement costs of £16.815m and base costs of £2.181m [CE.A1 P49]. The company identifies that the RGF refurb and contact tank elements of the scheme are excluded from the enhancement cost [CE.A1 P51]. We estimate that a contact tank volume of approximately 2800m3 is required to give a 30 minute retention time at full flow. Given the potential cost of a tank of this volume and the RGF refurbishment we expect a breakdown of scheme costs We find insufficient evidence to justify the division of costs between base and enhancement proposed by the company we therefore apply a 20% challenge and pass £13.451m [£16.821*(1-.20)]. We then apply a company specific cost challenge and make an allowance of £12.779m. Opex: Yorkshire Water is seeking £0.193m opex allowance all of which is allocated to the water treatment price control. The company identifies opex spend is associated with the work at Tophill Low WTW[CE.A1 P49] . Our modelling of treatment costs includes a WTW complexity variable. Therefore operational cost of the enhanced works is included in our base modelled costs and we make no allowance for opex as part of this assessment. | CE.A1 Securing Cost Efficiency | Partial pass | Work is at Tophill Low - a 65Ml/d? DO WTW. This work includes refurbishment / inter-stage ozone / GAC absorbers / contact tank. Some elements should be allocated to base expenditure for example RGF refurb. The contact tank is justified on the basis that the site doesn’t have a dedicated asset standard disinfection contact tank as is preferred for a river fed works, [App14a Pt. B P79]. The scheme is also identified as delivering resilience benefits. we apply a deduction of 20% as scheme is not least whole life cost together with a further 10% as scheme includes provision of 'asset standard contact tank' as this element is considered to be base maintenance. We find a scheme level cost of £16.3m [App14a Table 1 P10] to which we apply a total challenge of 30% to give £11.41m to which we apply the company efficiency challenge. | App 14a Pt. B P79 App14a P10.
Customer protection | Pass | The company has not raised substantive issues in its representation and we retain our draft determination assessment regarding this gate. |  | Customer protection | Pass | Assessment unchanged from IAP. |  | Pass | Customers are protected by the DWI Letter of support. YKY has an ODI with penalty payments. | DWI Letter of support Appendix 19C 26 Drinking Water Contacts.
Affordability | N/A |  |  | Affordability | N/A |  |  | N/A
Board assurance | N/A |  |  | Board assurance | N/A |  |  | N/A
Further analysis / arguments
Information from the DWI letter of support is summarised as:
* Tophill Low- Taste, Odour (T&O) and Cryptosporidium - Provision of treatment facilities at Tophill Low WTW to secure compliance with the Taste and Odour drinking water quality standards, and to reduce the risk of Cryptosporidium - Estimated Capex - £16.3m - Crypto is a RW deterioration risk but retain YKY's line allocation.

## Deep dive_SSC
Deep dive sheet - South Staffs Water |  |  |  | Summary at DD
Summary |  |  |  | Summary
Company | SSC |  |  | Company | SSC
Control | Wholesale water |  |  | Control | Wholesale water
Totex carried through deep dive AMP7 (£m) | 0 | For draft determination the company requested £74.346m totex . For final determination the company requests £68.454m in its August business plan WS2 table submission. |  | Totex carried through deep dive AMP7 (£m) | 0
Totex assessed within cost adjustment claims (£m) |  |  |  | Totex assessed within cost adjustment claims (£m) |  |  |  | Summary at IAP
Totex assessed within deep dive (£m) | 0 |  |  | Totex assessed within deep dive (£m) | 0
Totex allowance from cost adjustment claims (£m) | 68.023 |  |  | Totex allowance from cost adjustment claims (£m) | 62.8952 |  |  | Assessment was made as Cost Adjustment Claim
Totex allowance from deep dive (£m) |  |  |  | Totex allowance from deep dive (£m)
Ofwat view of totex allowance for AMP7 (£m) | 68.023 | As at draft determination we assess this as a cost adjustment claim. |  | Ofwat view of totex allowance for AMP7 (£m) | 62.8952
Assessment |  |  |  | Assessment
Assessment gates |  |  | References | Assessment gates |  |  | References
Need for investment | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Need for investment | N/A | Assessment undertaken as cost adjustment claim
Need for adjustment | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Need for adjustment | N/A | Assessment undertaken as cost adjustment claim
Management control | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Management control | N/A | Assessment undertaken as cost adjustment claim
Best option for customers | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Best option for customers | N/A | Assessment undertaken as cost adjustment claim
Robustness and efficiency of costs | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Robustness and efficiency of costs | N/A | Assessment undertaken as cost adjustment claim
Customer protection | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Customer protection | N/A | Assessment undertaken as cost adjustment claim
Affordability | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Affordability | N/A | Assessment undertaken as cost adjustment claim
Board assurance | N/A | As at draft determination. Assessment is made as a cost adjustment claim. |  | Board assurance | N/A | Assessment undertaken as cost adjustment claim

## Allowance
Allowed costs
| Assessor's initials | RP
| Peer review (initials, date) | AF, 6/12/19
| BoN code | W3003CAW + WS2013CAW
| Enhancement line | Improving taste / odour / colour
Cost allowance for AMP7 (£m)
| Company | Totex in business plan - wholesale water | Net totex reallocated in | Totex after reallocations | Modelled allowance | Totex allowed wholesale water | Totex allowed water resources | Totex allowed network plus |  | Proportion of water resources
1 | ANH | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
2 | HDD | 1.8129 | 0 | 1.8129 | 1.3423 | 1.3423 | 0.16071 | 1.1816 | Deep dive | 11.97%
3 | NES | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
4 | NWT | 11.8521 | 0 | 11.8521 | 11.8521 | 11.8521 | 0.25468 | 11.5975 | Shallow dive | 2.149%
5 | SRN | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
6 | SVE | 11.328 | 0 | 11.328 | 11.328 | 11.328 | 0 | 11.328 | Shallow dive | 0%
7 | SWB | 7.8 | 0 | 7.8 | 7.41 | 7.41 | 0 | 7.41 | Deep dive | 0%
8 | TMS | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
9 | WSH | 27.219 | 0 | 27.219 | 96.8656 | 96.8656 | 0 | 96.8656 | Deep dive | 0%
10 | WSX | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
11 | YKY | 17.007 | 0 | 17.007 | 12.7786 | 12.7786 | 0 | 12.7786 | Deep dive | 0%
12 | AFW | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
13 | BRL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
14 | PRT | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
15 | SES | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
16 | SEW | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
17 | SSC | 74.349 | 0 | 74.349 | 68.023 | 68.023 | 0 | 68.023 | Deep dive | 0%
| Total | 151.3681 | 0 | 151.3681 | 209.5997 | 209.5997 | 0.41538 | 209.1843